## FCI Summary
Building Name: | Peshine Ave | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 124385
Number of Floors: | B + 4
School Age (years): | 101
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 53.46%
Facility Condition = | VERY POOR
FCI Deficiency Cost = | 13715929.8832
FCI Replacement Cost = | 25654406.25
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 572
Historic 2005 LRFP Capacity = | 814
Adjusted 2012 Capacity = | 824
Recent Occupancy % = | 69.42%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 92.27%
Classroom Adequacy = | GOOD
Special Spaces Adequacy % Score = | 74.86%
Special Spaces Adequacy = | POOR

## Uniformat FCI
Building Name: |  | Peshine Ave | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 124385
Largest Floor Level Area: |  | 32085
Vertical FAR Ratio: |  | 3.8767
School Age (years): |  | 101
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 1.8% | 3.7125 | 124385 | 461779.3125 | 100 | 101 | 0 | 0.5 | 5 | 5 | 23088.9656 | 438690.3469 | 95%
|  |  | A1030 - SLAB ON GRADE | 1.5% | 3.0938 | 124385 | 384816.0938 | 100 | 101 | 0 | #DIV/0! | 5 | 5 | 19240.8047 | 365575.2891 | 95%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 124385 | 564396.9375 | 100 | 101 | 0 | 0.5 | 5 | 5 | 28219.8469 | 536177.0906 | 95%
|  |  | SUBTOTAL SUBSTRUCTURE | 5.5% | 11.3438 | 124385 | 1410992.3438
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 124385 | 2821984.6875 | 100 | 101 | 0 | 0.625 | 5 | 5 | 141099.2344 | 2680885.4531 | 95%
|  |  | B1020 - ROOF CONSTRUCTION | 2.5% | 5.1562 | 124385 | 641360.1562 | 100 | 101 | 0 | 0.5 | 5 | 5 | 32068.0078 | 609292.1484 | 95%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 9.5% | 19.5938 | 124385 | 2437168.5938 | 100 | 101 | 0 | 0.4625 | 5 | 5 | 121858.4297 | 2315310.1641 | 95%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 5.5% | 11.3438 | 124385 | 1410992.3438 | 30 | 35.5 | 0 | 0.25 | 5 | 5 | 235165.3906 | 1175826.9531 | 83.33%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 2% | 4.125 | 124385 | 513088.125 | 30 | 18.8571 | 11.1429 | 0.46429 | 13.9286 | 25.0714 | 428795.0759 | 84293.0491 | 16.43%
|  |  | SUBTOTAL SHELL | 30.5% | 62.9063 | 124385 | 7824593.9063
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 124385 | 1026176.25 | 60 | 54.4103 | 5.5897 | 0.57692 | 34.6154 | 40.2051 | 687625.7949 | 338550.4551 | 32.99%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 124385 | 384816.0938 | 20 | 23.2439 | 0 | 0.45732 | 5 | 5 | 96204.0234 | 288612.0703 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 124385 | 1026176.25 | 20 | 7.5 | 12.5 | 0.75 | 15 | 20 | 1026176.25 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 124385 | 384816.0938 | 30 | 101 | 0 | 0.5 | 5 | 5 | 64136.0156 | 320680.0781 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 4% | 8.25 | 124385 | 1026176.25 | 10 | 11.4286 | 0 | 0.54762 | 5 | 5 | 513088.125 | 513088.125 | 50%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 124385 | 1539264.375 | 20 | 19.2619 | 0.7381 | 0.39524 | 7.9048 | 8.6429 | 665182.1049 | 874082.2701 | 56.79%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 124385 | 1539264.375 | 30 | 29.8974 | 0.10256 | 0.44103 | 13.2308 | 13.3333 | 684117.5 | 855146.875 | 55.56%
|  |  | SUBTOTAL INTERIORS | 27% | 55.6875 | 124385 | 6926689.6875
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 0.7% | 1.4438 | 124385 | 179580.8438 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 179580.8438 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 124385 | 384816.0938 | 60 | 27.0618 | 32.9382 | 0.46849 | 28.1093 | 60 | 384816.0938 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 124385 | 333507.2812 | 60 | 18.5 | 41.5 | 0.5 | 30 | 60 | 333507.2812 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 124385 | 307852.875 | 60 | 38 | 22 | 0.5 | 30 | 52 | 266805.825 | 41047.05 | 13.33%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 124385 | 128272.0312 | 30 | 7.5 | 22.5 | 0.75 | 22.5 | 30 | 128272.0312 | 0 | 0%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 3.2% | 6.6 | 124385 | 820941 | 60 | 0 | 60 | 0 | 0 | 60 | 820941 | 0 | 0%
|  |  | D3020 - BOILERS | 2.5% | 5.1562 | 124385 | 641360.1562 | 60 | 7.5 | 52.5 | 0.625 | 37.5 | 60 | 641360.1562 | 0 | 0%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4.5% | 9.2812 | 124385 | 1154448.2812 | 40 | 35.25 | 4.75 | 0.375 | 15 | 19.75 | 570008.8389 | 584439.4424 | 50.62%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4.5% | 9.2812 | 124385 | 1154448.2812 | 40 | 28.3102 | 11.6898 | 0.38565 | 15.4259 | 27.1157 | 782593.0073 | 371855.2739 | 32.21%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 0% | 0 | 124385 | 0 | 40 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | #DIV/0!
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.8% | 3.7125 | 124385 | 461779.3125 | 20 | 0 | 20 | 0 | 0 | 20 | 461779.3125 | 0 | 100%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 124385 | 256544.0625 | 20 | 0 | 20 | 0 | 0 | 20 | 256544.0625 | 0 | 100%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 124385 | 51308.8125 | 20 | 24.25 | 0 | 0.5 | 5 | 5 | 12827.2031 | 38481.6094 | 75%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 124385 | 333507.2812 | 60 | 38 | 22 | 0.5 | 30 | 52 | 289039.6437 | 44467.6375 | 13.33%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 124385 | 1795808.4375 | 30 | 22.4583 | 7.5417 | 0.65486 | 19.6458 | 27.1875 | 1627451.3965 | 168357.041 | 9.375%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 124385 | 769632.1875 | 20 | 21.1 | 0 | 0.45 | 5 | 5 | 192408.0469 | 577224.1406 | 75%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 124385 | 76963.2188 | 20 | 35.2952 | 0 | 0.40952 | 5 | 5 | 19240.8047 | 57722.4141 | 75%
|  |  | SUBTOTAL SERVICES | 34.5% | 71.1562 | 124385 | 8850770.1562
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 124385
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 124385
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 124385
|  |  | E1090 - OTHER EQUIPMENT |  |  | 124385
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 124385
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 124385
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 124385
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 124385
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 124385
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 124385 | 256544.0625 | 30 | 0 | 30 | 0.25 | 7.5 | 30 | 256544.0625 | 0 | 0%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 124385 | 128272.0312 | 30 | 30 | 0 | 0.5 | 15 | 15 | 64136.0156 | 64136.0156 | 50%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 124385 | 128272.0312 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 32068.0078 | 96204.0234 | 75%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 124385 | 128272.0312 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 32068.0078 | 96204.0234 | 75%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 124385 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 124385
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 124385 | 25654406.25 | [7 empty] | 13715929.8832 | 53.46%
100%
Note on J36: Tessier, Matthew: No Survey Data
Note on J41: Tessier, Matthew: No Survey Data
Note on J42: Tessier, Matthew: No Survey Data
Note on J58: Tessier, Matthew: No Survey Data

## Master File (Interior)
Peshine Avenue
School Code: | 600
NPS Code: | 88
Street: | 433 Peshine Ave.
City/Town: | Newark,
Database ID: | 40
Total size (gsf): | 125354
ROOM INFORMATION | [11 empty] | Average Age | 54.6429 | Ave Condition | 0.5 | [5 empty] | Average Age | 19.2619 | Ave Condition | 0.39524 | [5 empty] | Average Age | 11.4286 | Ave Condition | 0.54762 | [5 empty] | Average Age | 29.8974 | Ave Condition | 0.44103 | [5 empty] | Average Age | 23.2439 | Ave Condition | 0.45732 | [5 empty] | Average Age | 54.4103 | Ave Condition | 0.57692 | [5 empty] | Average Age | 27.1333 | Ave Condition | 0.37667 | [5 empty] | Average Age | 27.6875 | Ave Condition | 0.40625 | [5 empty] | Average Age | 26.9167 | Ave Condition | 0.45833 | [5 empty] | Average Age | 30 | Ave Condition | 0.45833 | [5 empty] | Average Age | 23.5714 | Ave Condition | 0.64286 | [5 empty] | Average Age | 7.5 | Ave Condition | 0.75 | [5 empty] | Average Age | 14.9167 | Ave Condition | 0.55972 | [5 empty] | Average Age | 29.8857 | Ave Condition | 0.47857 | [5 empty] | Average Age | 29.4861 | Ave Condition | 0.45139 | [5 empty] | Average Age | 15.4444 | Ave Condition | 0.45556 | [5 empty] | Average Age | 24.25 | Ave Condition | 0.5 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 10 | Ave Condition | 0.5 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [8 empty] | Plumbing Fixtures - Urinals | [8 empty] | Plumbing Fixtures - Showers | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
1428 | 11 | Storage | Basement | A | Support |  |  | 855 | 9' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1429 | 12 | Music Room | Basement | A | Visual & Performing Arts |  |  | 842 | 9' 6" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Specialty Ceilings (describe) | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Poor | 0.25 |  |  | Terracotta masonry partition | [6 empty] | 0 |  | N/A | [35 empty] | N/A | [9 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Ceiling radiant heat | [8 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | [18 empty] | N/A | [115 empty] | Present
1430 | 13 | Classroom | Basement | A | General Classroom |  |  | 1199 | 10' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1431 | 14 | Classroom | Basement | A | General Classroom |  |  | 1087 | 10' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1432 | UN-1 | Storage | Basement | A | Support |  |  | 605 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1433 | UN-2 | Cafeteria | Basement | B | Food Service/Assembly (K-8) |  |  | 4028 | 9' 8" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 |  |  | Surface/Glue applied | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | [9 empty] | 0 |  | N/A | [27 empty] | Wall Mounted China Drinking Fountains | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [11 empty] | N/A | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 | [10 empty] | Present | Pull station | [17 empty] | N/A | [8 empty] | N/A | [106 empty] | Present | [35 empty] | Present
1434 | UN-3 | Kitchen | Basement | B | Food Service/Assembly (K-8) |  |  | 546 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Tile | 46 | 60 | 53 | Good | 0.75 |  |  |  | In-Counter Lavatories | 16 | 21 | 18.5 | Good | 0.75 |  |  | Sinks | [35 empty] | N/A | [9 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Fair | 0.5 | [11 empty] | N/A | Wet Chemical | 30+ |  | 30 | Fair | 0.5 | [10 empty] | Present | [18 empty] | N/A | [8 empty] | N/A | [106 empty] | Present | [35 empty] | Present
1435 | UN-4 | Storage | Basement | A | Support |  |  | 137 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1436 | UN-5 | Storage | Basement | A | Support |  |  | 147 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1437 | UN-6 | Water Closet | Basement | A | Support |  |  | 30 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1438 | UN-7 | N/A | Basement | A | N/A |  |  | 321 | N/A
1439 | UN-8 | N/A | Basement | A | N/A |  |  | 43 | N/A
1440 | UN-9 | Storage | Basement | A | Support |  |  | 59 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1441 | UN-10 | N/A | Basement | A | N/A |  |  | 208 | N/A
1442 | UN-11 | Custodial Closet | Basement | A | Support |  |  | 37 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1443 | UN-12 | Storage | Basement | A | Support |  |  | 40 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1444 | UN-13 | Women's Water Closet | Basement | A | Support |  |  | 355 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1445 | UN-14 | Storage | Basement | A | Support |  |  | 1069 | 9' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1446 | UN-15 | Storage | Basement | A | Support |  |  | 971 | 9' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1447 | UN-16 | Custodial Office | Basement | A | Support |  |  | 825 | 9' 10" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Other (describe) | 20+ |  | 20 | Poor | 0.25 | 0 |  | Exposed concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Poor | 0.25 | 0 |  | Brick with wood dividers | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 |  | Sink | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [17 empty] | N/A | [9 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 PC | [106 empty] | Present | Verizon telephone panel board
1448 | UN-17 | Girls' Water Closet | Basement | A | Support |  |  | 271 | 9' 10" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 2 |  | Sinks | Wall Hung Flush Valve | 30+ |  | 30 | Fair | 0.5 | 5 | [8 empty] | 0 | [19 empty] | N/A | Metal, Powder Coated | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 |  |  | Fan coil unit | [8 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | [134 empty] | Present
1449 | UN-18 | Storage | Basement | A | Support |  |  | 64 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1450 | UN-19 | Storage | Basement | A | Support |  |  | 486 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1452 | UN-21 | Boiler Room | Basement | A | Support |  |  | 1902 | N/A
1453 | UN-22 | Storage | Basement | A | Support |  |  | 223 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1454 | UN-23 | Book Room | Basement | A | Support |  |  | 936 | 9' 10" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [17 empty] | N/A | [8 empty] | N/A | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [11 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | [18 empty] | N/A | [8 empty] | N/A | [106 empty] | Present
1455 | UN-24 | Child Study Team | Basement | A | Administration |  |  | 187 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1456 | UN-25 | Small Group Instruction | Basement | A | Small Group Instruction |  |  | 248 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1457 | UN-26 | Small Group Instruction | Basement | A | Small Group Instruction |  |  | 160 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1458 | UN-27 | Small Group Instruction | Basement | A | Small Group Instruction |  |  | 213 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1459 | UN-28 | Gym | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 3175 | H:27' 0"; L:19' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Specialty Ceilings (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Unfinished Planks | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | HID Vapor Pendant Mount Fixture | 0 | 7 | 3.5 | Poor | 0.25 | 0 |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [16 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [15 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [69 empty] | 0 | Present
1460 | UN-29 | Storage | Basement | A | Support |  |  | 842 | 9' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1461 | UN-30 | Storage | Basement | A | Support |  |  | 879 | 9' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1462 | UN-31 | Boys' Water Closet | Basement | A | Support |  |  | 307 | 9' 6" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 3 |  | Sinks | Wall Hung Flush Valve | 30+ |  | 30 | Fair | 0.5 | 3 | [8 empty] | 4 | [20 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 |  |  | Ceiling and wall mount fluorescent | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Fan coil unit | [8 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | [18 empty] | N/A | [8 empty] | N/A | [106 empty] | Present
1463 | UN-32 | Storage | Basement | A | Support |  |  | 57 | 9' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1464 | 101 | Kindergarten Classroom | Ground Floor | A | Kindergarten Classroom |  |  | 842 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | With folding partition | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [8 empty] | N/A | [8 empty] | N/A | [9 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 3 | [72 empty] | Present
1465 | 102 | Kindergarten Classroom | Ground Floor | A | Kindergarten Classroom |  |  | 377 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1466 | 104 | Science Classroom | Ground Floor | A | Science (6-12) |  |  | 823 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 2012-11-15 |  | 1900-01-12 | Poor | 0.25 | 0 |  | Worn areas | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  | Painted walls with wainscot, water damage | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  | Unit ventilator trane unit | [6 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 1 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | water saver fausset company | [6 empty] | 0 | [26 empty] | 0 | Present
1467 | 105 | Classroom | Ground Floor | A | General Classroom |  |  | 831 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1468 | 106 | Classroom | Ground Floor | A | General Classroom |  |  | 840 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  | water damage | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 2 | [71 empty] | 0 | Present
1469 | 107 | Classroom | Ground Floor | A | General Classroom |  |  | 847 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 3 | [72 empty] | Present
1470 | 108 | Kindergarten Classroom | Ground Floor | A | Kindergarten Classroom |  |  | 852 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1471 | 109 | Kindergarten Classroom | Ground Floor | A | Kindergarten Classroom |  |  | 877 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1472 | 110 | Kindergarten Classroom | Ground Floor | A | Kindergarten Classroom |  |  | 842 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1473 | 111 | K-2nd Grade Classroom | Ground Floor | A | General Classroom |  |  | 784 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1474 | 112 | K-2nd Grade Classroom | Ground Floor | A | General Classroom |  |  | 789 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1475 | 113 | K-2nd Grade Classroom | Ground Floor | B | General Classroom |  |  | 794 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 2012-11-15 |  | 1900-01-12 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed splines | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [8 empty] | 0 |  | N/A | [45 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 3 | [71 empty] | 0 | Present
1476 | 114 | 1st-3rd Grade Classroom | Ground Floor | B | General Classroom (Grades 1-3) |  |  | 798 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed splaines | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  | Not closing | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  | Sink | [45 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 3 | [71 empty] | 0 | Present
1477 | 115 | 1st-3rd Grade Classroom | Ground Floor | A | General Classroom (Grades 1-3) |  |  | 808 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1478 | 116 | 1st-3rd Grade Classroom | Ground Floor | A | General Classroom (Grades 1-3) |  |  | 799 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1479 | 117 | Classroom | Ground Floor | B | General Classroom |  |  | 747 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [8 empty] | 0 |  | N/A | [45 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 3 | [71 empty] | 0 | Present
1480 | 118 | Classroom | Ground Floor | A | General Classroom |  |  | 759 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1481 | 119 | 1st-3rd Grade Classroom | Ground Floor | A | General Classroom (Grades 1-3) |  |  | 750 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1482 | UN-33 | Girls' Water Closet | Ground Floor | A | Support |  |  | 273 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 3 | [8 empty] | 6 | [8 empty] | 0
1483 | UN-34 | Custodial Closet | Ground Floor | A | Support |  |  | 37 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1484 | UN-35 | Custodial Closet | Ground Floor | A | Support |  |  | 31 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1485 | UN-36 | Boys' Water Closet | Ground Floor | A | Support |  |  | 243 | 8' 4" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Ceramic Tile Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  | with wainscot | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 2 |  |  | Wall Hung Flush Valve | 30+ |  | 30 | Fair | 0.5 | 5 |  |  | Wall Hung | 30+ |  | 30 | Fair | 0.5 | 6 | [17 empty] | 0 |  | N/A | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  | composite | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [16 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A
1486 | UN-37 | Storage | Ground Floor | A | Support |  |  | 60 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1487 | UN-38 | Vice Principal Office | Ground Floor | A | Administration |  |  | 284 | 9' 10" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed splines | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  | Window AC unit | [6 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [108 empty] | Present
1488 | UN-39 | Water Closet | Ground Floor | A | Administration |  |  | 34 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1489 | UN-40 | Water Closet | Ground Floor | A | Administration |  |  | 33 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1490 | UN-41 | Girls' Water Closet | Ground Floor | A | Support |  |  | 317 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1491 | UN-42 | Storage | Ground Floor | A | Support |  |  | 44 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1492 | UN-43 | Conference Room | Ground Floor | A | Administration |  |  | 180 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1493 | UN-44 | Principal's Office | Ground Floor | A | Administration |  |  | 159 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 22 | 30 | 26 | Fair | 0.5 | 0 |  | Window Ac unit | [6 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [108 empty] | Present
1494 | UN-45 | Main Office | Ground Floor | A | Administration |  |  | 220 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  | Window Ac | [6 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [108 empty] | Present
1495 | UN-46 | N/A | Ground Floor | A | N/A |  |  | 802 | 12' 0"
1496 | UN-47 | Auditorium | Ground Floor | A | Visual & Performing Arts |  |  | 3318 | 24' 3" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Good | 0.75 | [9 empty] | 0 |  | N/A | [35 empty] | N/A | [9 empty] | HID Surface Mount Fixture | 0 | 7 | 3.5 | Very Good | 0.9 |  |  | Mercury Halide | [8 empty] | Not visible | Cast Iron Radiators | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | [11 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | Fire pull stattion | [17 empty] | N/A | [8 empty] | N/A | [106 empty] | Present | Audio systems
1497 | UN-48 | Storage | Ground Floor | A | Visual & Performing Arts |  |  | 228 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1498 | UN-49 | Storage | Ground Floor | A | Support |  |  | 230 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1499 | UN-50 | Gym Balcony | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 342 | H: 18' 0"; L:10' 0" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1500 | UN-51 | Boys' Water Closet | Ground Floor | A | Support |  |  | 306 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 3 | [8 empty] | 3 | [8 empty] | 4
1501 | UN-52 | Storage | Ground Floor | A | Support |  |  | 57 | 8' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1502 | 201 | Classroom | 1st Floor | A | General Classroom |  |  | 840 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  | Concrete | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [7 empty] | Present | [9 empty] | N/A | [6 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 4 | [72 empty] | Present
1503 | 202 | Classroom | 1st Floor | A | General Classroom |  |  | 816 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  | Concrete | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | N/A | [15 empty] | 0 |  | N/A | [6 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [19 empty] | N/A | [8 empty] | N/A | [78 empty] | 0 | Present
1504 | 203 | Classroom | 1st Floor | A | General Classroom |  |  | 845 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1505 | 204 | Classroom | 1st Floor | A | General Classroom |  |  | 822 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1506 | 205 | Small Group Instruction | 1st Floor | A | Small Group Instruction |  |  | 835 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1507 | 206 | Computer Lab | 1st Floor | A | Technological Literacy |  |  | 842 | 11' 11" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  | Water damage | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  | Water damage | Plaster | 30+ |  | 30 | Very Poor | 0.1 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | N/A | Wall-Mounted Lavatories | 30+ |  | 30 | Very Good | 0.9 |  |  | Not operational | [45 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 16 | 21 | 18.5 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [26 empty] | 0 |  | N/A | [6 empty] | 9 | [72 empty] | Present
1508 | 207 | Classroom | 1st Floor | A | General Classroom |  |  | 842 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1509 | 208 | Classroom | 1st Floor | A | General Classroom |  |  | 855 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1510 | 209 | Classroom | 1st Floor | A | General Classroom |  |  | 879 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1511 | 210 | Classroom | 1st Floor | A | General Classroom |  |  | 844 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1512 | 213 | Classroom | 1st Floor | A | General Classroom |  |  | 794 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1513 | 214 | Classroom | 1st Floor | A | General Classroom |  |  | 796 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1514 | 215 | 5th Grade Classroom | 1st Floor | B | General Classroom (Grades 4-5) |  |  | 811 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1515 | 216 | Classroom | 1st Floor | A | General Classroom |  |  | 799 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1516 | 217 | 3rd-5th Grade Classroom | 1st Floor | A | General Classroom (Grades 4-5) |  |  | 747 | 9' 9" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1517 | 218 | 3rd-5th Grade Clasroom | 1st Floor | B | General Classroom (Grades 4-5) |  |  | 759 | 9' 9" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 |  | Sink | [45 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [26 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1518 | 219 | 5th Grade Clasroom | 1st Floor | A | General Classroom (Grades 4-5) |  |  | 750 | 9' 9" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1519 | UN-53 | Library | 1st Floor | B | Media Center |  |  | 1341 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Carpet | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 16 | 30 | 23 | Fair | 0.5 | 0 |  | Interior accordion for room 213/ curtain wall between UN63 | [8 empty] | N/A | [45 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Fan coil | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  | AC unit | [6 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1520 | UN-54 | Girls' Water Closet | 1st Floor | A | Support |  |  | 272 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 3 | [8 empty] | 6 | [8 empty] | 0
1521 | UN-55 | 1st-2nd Grade Supply Room | 1st Floor | A | Support |  |  | 36 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1522 | UN-56 | Custodial Closet | 1st Floor | A | Support |  |  | 31 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1523 | UN-57 | Boys' Water Closet | 1st Floor | A | Support |  |  | 240 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 6
1524 | UN-58 | Storage | 1st Floor | A | Support |  |  | 61 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1525 | UN-59 | Teachers\' Room | 1st Floor | B | Faculty Support |  |  | 282 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [56 empty] | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 | 0 |  | Original pendant | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 16 | 21 | 18.5 | Very Poor | 0.1 | 0 |  | AC unit | [6 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1526 | UN-60 | Women's Water Closet | 1st Floor | A | Faculty Support |  |  | 36 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1527 | UN-61 | Men's Water Closet | 1st Floor | A | Faculty Support |  |  | 34 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1528 | UN-62 | Office | 1st Floor | A | Administration |  |  | 115 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1529 | UN-63 | Office | 1st Floor | A | Administration |  |  | 108 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1530 | UN-64 | Girls' Water Closet | 1st Floor | A | Support |  |  | 317 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1531 | UN-65 | Storage | 1st Floor | A | Support |  |  | 43 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1532 | UN-66 | Girls' Water Closet | 1st Floor | A | Support |  |  | 265 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1533 | UN-67 | Storage | 1st Floor | A | Support |  |  | 71 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1534 | UN-68 | Auditorium | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 725 | 12' 0" | [9 empty] | Wood | [17 empty] | Plaster
1535 | UN-69 | Boys' Water Closet | 1st Floor | A | Support |  |  | 307 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 3 | [8 empty] | 3 | [8 empty] | 4
1536 | UN-70 | Storage | 1st Floor | A | Support |  |  | 57 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1537 | 301 | 7th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 842 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1538 | 302 | 7th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 819 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  | Painted plaster | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  | AC unit | [6 empty] | 0 | [26 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1539 | 303 | 7th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 846 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1540 | 304 | 7th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 826 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1541 | 305 | Small Group Instruction | 2nd Floor | A | Small Group Instruction |  |  | 833 | 11' 11" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1542 | 306 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 840 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1543 | 307 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 840 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 2012-11-15 |  | 1900-01-12 | Very Poor | 0.1 | 0 |  | Water damage | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Very Poor | 0.1 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 16 | 21 | 18.5 | Poor | 0.25 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1544 | 308 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 855 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1545 | 309 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 882 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1546 | 310 | Computer Lab | 2nd Floor | A | Technological Literacy |  |  | 844 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  | AC unit | [6 empty] | 0 | [9 empty] | Present | Motion sensors, separately alarmed smoke detectors | [15 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1547 | 311 | 4th Grade Classroom | 2nd Floor | B | General Classroom (Grades 4-5) |  |  | 780 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 |  | sink | [45 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1548 | 312 | Classroom | 2nd Floor | A | General Classroom |  |  | 793 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1549 | 313 | Classroom | 2nd Floor | A | General Classroom |  |  | 796 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1550 | 314 | Small Group Instruction | 2nd Floor | B | Small Group Instruction |  |  | 796 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  | surface/Glue applied | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  | Glazed | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Stainless Steel Sinks | 16 | 21 | 18.5 | Poor | 0.25 | 1 |  | Sink and fountain | [45 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Fan coil unit | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [26 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1551 | 315 | Science Classroom | 2nd Floor | B | Science (6-12) |  |  | 811 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  | surface glue applied | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Poor | 0.25 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Fan coil unit | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [62 empty] | Present
1552 | 316 | 3rd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 797 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1553 | 317 | 3rd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 749 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1554 | 318 | 4th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 759 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1555 | 319 | 5th Grade Classroom | 2nd Floor | B | General Classroom (Grades 4-5) |  |  | 750 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Poor | 0.25 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Fan coil unit | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [7 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [70 empty] | Present
1556 | UN-71 | Girls' Water Closet | 2nd Floor | B | Support |  |  | 272 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 3 |  | Sinks | Wall Hung Flush Valve | 30+ |  | 30 | Fair | 0.5 | 6 | [8 empty] | 0 |  | N/A | [17 empty] | N/A | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 |  |  | 1x6 Wall mounted Fluorescent | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Fan coil unit | [8 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | [18 empty] | N/A | [8 empty] | N/A
1557 | UN-72 | Storage | 2nd Floor | A | Support |  |  | 37 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1558 | UN-73 | Custodial Closet | 2nd Floor | A | Support |  |  | 31 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1559 | UN-74 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 241 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 6
1560 | UN-75 | Storage | 2nd Floor | A | Support |  |  | 61 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1561 | UN-76 | Teachers' Lounge | 2nd Floor | B | Faculty Support |  |  | 283 | 9' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  | Surface glue applied | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [17 empty] | N/A | [8 empty] | N/A | Fluorescent Pendant Mount Fixture | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Fan coil unit | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Poor | 0.25 | 0 |  | AC unit | [6 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [108 empty] | Present
1562 | UN-77 | Men's Water Closet | 2nd Floor | A | Faculty Support |  |  | 36 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1563 | UN-78 | Women's Water Closet | 2nd Floor | A | Faculty Support |  |  | 34 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1564 | UN-79 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 315 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1565 | UN-80 | Storage | 2nd Floor | A | Support |  |  | 43 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1566 | UN-81 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 265 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1567 | UN-82 | Storage | 2nd Floor | A | Support |  |  | 72 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1568 | UN-83 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 308 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 3 | [8 empty] | 3 | [8 empty] | 4
1569 | UN-84 | Storage | 2nd Floor | A | Support |  |  | 58 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1570 | UN-85 | Water Closet | 3rd Floor | A | Support |  |  | 38 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1571 | UN-86 | Water Closet | 3rd Floor | A | Support |  |  | 72 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1572 | UN-87 | Music Room | 3rd Floor | A | Visual & Performing Arts |  |  | 915 | 12' 0" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [33 empty] | 0 |  | N/A | [9 empty] | Fluorescent Pendant Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [16 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1573 | UN-88 | Office | 3rd Floor | A | Administration |  |  | 90 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1574 | UN-89 | Storage | 3rd Floor | A | Faculty Support |  |  | 47 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
2 | A | Main Entrance | 1st floor | [6 empty] | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Other (describe) | 20+ |  | 20 | Fair | 0.5 |  |  | Painted concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  | Isolated water damage | Plaster | 30+ |  | 30 | Fair | 0.5 | [11 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 | [11 empty] | Unknown | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wet Chemical | 30+ |  | 30 | Good | 0.75 |  |  | Wall mount | [7 empty] | Present | Smoke and heat detectors | [25 empty] | Present | Paging Phone
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
2 | A | Corridor #2 | 1st floor | Old | [5 empty] | Other (describe) | 20+ |  | 20 | Fair | 0.5 | 0 |  | Painted concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wet Chemical | 30+ |  | 30 | Good | 0.75 | 0 |  | Wall mount | [6 empty] | 0 | Present | Smoke and heat detectors | [24 empty] | 0 | Present | Paging phone
3 | B | Corridor #3 | 1st floor | Addition | [5 empty] | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | [11 empty] | N/A | Plaster/Metal Stud Framing | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Wall Mounted China Drinking Fountains | 30+ |  | 30 | Good | 0.75 | [11 empty] | N/A | Fluorescent Recessed Fixture | 30+ |  | 30 | Poor | 0.25 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wet Chemical | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | [10 empty] | Present | Smoke and heat detectors | [16 empty] | Present | Camera | [7 empty] | Present | Audible fire alarm bells
4 | C | Corridor #1 | Basement | Old(Presents unlock electric panel) | [5 empty] | Other (describe) | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  | Painted plaster | Plaster | 30+ |  | 30 | Poor | 0.25 | [11 empty] | N/A | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [11 empty] | N/A | [8 empty] | N/A | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wet Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present | Smoke and heat detectors | [16 empty] | Present | Camera | [7 empty] | Present | Paging phone
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
2 | A | Stairwell #1 | Basement | [6 empty] | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Reinforced Concrete | 30+ |  | 30 | Very Good | 0.9 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | [11 empty] | N/A | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [11 empty] | N/A | [7 empty] | Present | Smoke and heat detectors | [16 empty] | Present | Camera
3 | B | Stairwell #5 | 1st floor | [6 empty] | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Reinforced Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Terrazzo | 30+ |  | 30 | Poor | 0.25 |  |  |  | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [11 empty] | N/A | [7 empty] | Present | Smoke and heat detectors | [16 empty] | Present | Camera
EXTERIORs INFORMATION

## Master File (Systems)
Systems | Question | Value1 |  | Average1 | Value2 | Average2 | Systems | Question | Value1 | Average1
Systems | Seg ID | 31 |  |  | 32 |  | InfoTech | Seg ID | 7
| Bldg.Phase | A |  |  | B |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  | Addition | 0
| Year Built | 1911 |  |  | 1962 |  |  | Year Built | 1911
Domestic Water Heaters | Location | UN/20 |  |  |  |  | Entrance Facilities (Demarc or Cable Vault) | Location
| Description | Fuel/Fired Water Heater | [5 empty] | Description
| Age | 16 | 21 | 18.5 |  |  |  | Age
| Condition | Fair |  | 0.5 |  |  |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | [6 empty] | Notes
Sanitary Drainage | Location | Basement |  |  |  |  | Main Dist. Facility (MDF) | Location
| Description | Sanitary Drainage Piping Cleanouts | [5 empty] | Description
| Age | 31 | 45 | 38 |  |  |  | Age
| Condition | Fair |  | 0.5 |  |  |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | [6 empty] | Notes
Building Support (other) Plumbing Systems | Location | Basement |  |  |  |  | MDF, HVAC Terminal Units | Location
| Description | Other (describe) | [5 empty] | Description
| Age | 0 | 15 | 7.5 |  |  |  | Age
| Condition | Good |  | 0.75 |  |  |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | Copper, hot water supply to building | [5 empty] | Notes
Fuel Piping | Location | UN/20 |  |  |  |  | MDF, Packaged Terminal Air Conditioner | Location
| Description | Gas Piping | [5 empty] | Description
| Age | 0 | 15 | 7.5 |  |  |  | Age
| Condition | Good |  | 0.75 |  |  |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | Gas | [5 empty] | Notes
Fuel Pumps | Location | [5 empty] | Inter. Data Facility (IDF #1) | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Fuel Storage Tanks | Location | [5 empty] | IDF #1, HVAC Terminal Units | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Fuel Fired Boilers | Location | UN/20 |  |  |  |  | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers | [5 empty] | Description
| Age | 0 | 15 | 7.5 |  |  |  | Age
| Condition | Fair |  | 0.5 |  |  |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | 3 units, 4.5 Million BTU gas boilers | [5 empty] | Notes
Furnaces | Location | [5 empty] | Inter. Data Facility (IDF #2) | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Unit Ventilators | Location | 1st floor |  |  |  |  | IDF #2, HVAC Terminal Units | Location
| Description | Vertical HV (w/heating only) | [5 empty] | Description
| Age | 40+ |  | 40 |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | [6 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | [6 empty] | Notes
Fan Coil Units | Location | [5 empty] | IDF #2, Packaged Terminal Air Conditioner | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | [6 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Water Chillers | Location | [5 empty] | Inter. Data Facility (IDF #3) | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | [6 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Cooling Towers | Location | [5 empty] | IDF #3, HVAC Terminal Units | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | [6 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Packaged Terminal Air Conditioner | Location | [5 empty] | IDF #3, Packaged Terminal Air Conditioner | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | [6 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Hydronic Piping System | Location | [5 empty] | Inter. Data Facility (IDF #4) | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Pumps | Location | [5 empty] | IDF #4, HVAC Terminal Units | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Steam Piping System | Location | Basement |  |  |  |  | IDF #4, Packaged Terminal Air Conditioner | Location
| Description | Single/Pipe | [5 empty] | Description
| Age | 60+ |  | 60 |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | [6 empty] | Notes
HVAC Air Distribution | Location | [5 empty] | Inter. Data Facility (IDF #5) | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Air Handling Units | Location | [5 empty] | IDF #5, HVAC Terminal Units | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | [6 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
HVAC Fans | Location |  |  |  | Roof |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description |  |  |  | Hooded Roof Ventilators |  |  | Description
| Age |  |  |  | 41233 | 10.5 |  | Age
| Condition |  |  |  | Fair | 0.5 |  | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A |  |  | 5 Units |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location | [5 empty] | Backbone Cable Dist. | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Fire/Suppression (Standpipes), Water/Based | Location | [5 empty] | Horizontal Cable Dist. | Location
| Description | [6 empty] | Description
| Age | [6 empty] | Age
| Condition | [6 empty] | Condition
| CheckBox | [6 empty] | CheckBox
| Quantity | 0 | [5 empty] | Quantity
| Voltage | [6 empty] | Voltage
| Power Output | [6 empty] | Power Output
| Elec Power | [6 empty] | Elec Power
| Notes | N/A | [5 empty] | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | UN/20
| Description | Gas Engine Generators
| Age | 31 | 45 | 38
| Condition | Poor |  | 0.25
CheckBox
| Quantity | 0
| Voltage | 5 KW
Power Output
Elec Power
| Notes | Kohler
Facility Power Generation (Alternative Sources) | Location | UN/20
| Description | Other (describe)
| Age | 31 | 45 | 38
| Condition | Fair |  | 0.5
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | Basement
| Description | D5010 120
| Age | 31 | 45 | 38
| Condition | Fair |  | 0.5
CheckBox
| Quantity | 0
| Voltage | 460KW
Power Output
Elec Power
| Notes | 40/50
Voice Communication Terminal Equipment | Location | Basement
| Description | PDX/Key Systems
| Age | 40+ |  | 40
| Condition | Fair |  | 0.5
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | 1st floor
| Description | Public Address and Mass Notification Systems
| Age | 41233 |  | 10.5
| Condition | Fair |  | 0.5
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Video Surveillance Systems | Location | 1st floor
| Description | Analog Video Recording Devices
| Age | 0 | 10 | 5
| Condition | Poor |  | 0.25
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | Basement
| Description | Fire Alarm Annunciation Panels
| Age | 40+ |  | 40
| Condition | Fair |  | 0.5
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
| Notes | N/A
Other Equipment | Location
| Description | N/A
Age
Condition
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Systems | Question | Value1 |  | Average1 | Value2 |  | Average2 | Systems | Question | Value1 | Average1
Exterior | Seg ID | 48 |  |  | 39 |  |  | SiteElements | Seg ID | 17
| Bldg.Phase | A |  |  | B |  |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  |  | Addition | 0
| Year Built | 1911 |  |  | 1962 |  |  |  | Year Built | 1911
(Foundation) Walls for Subgrade Enclosures, Primary | Location | Typical |  |  | Typical |  |  | Roadways | Location | typical
| Description | Brick, Solid (Mass) |  |  | Concrete, Cast/In/Place |  |  |  | Description | Concrete
| Age | 60+ |  | 60 | 46 | 60 | 53 |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  | Condition | Fair | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location | [6 empty] | Parking Lots | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A |  |  | N/A |  |  |  | Notes | N/A
Standard Slabs On Grade, Primary | Location | [6 empty] | Pedestrian Plazas and Walkways, Primary | Location | Typical
| Description | [7 empty] | Description | Concrete, CIP
| Age | [7 empty] | Age | 30+ | 30
| Condition | [7 empty] | Condition | Fair | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A |  |  | N/A |  |  |  | Notes
Standard Slabs On Grade, Secondary | Location | [6 empty] | Pedestrian Plazas and Walkways, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A |  |  | N/A |  |  |  | Notes | N/A
Floor Construction, Primary | Location | Typical |  |  | Typical |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location
| Description | Wood, Beams and Joists |  |  | Concrete, CIP Beams and Slab |  |  |  | Description
| Age | 60+ |  | 60 | 46 | 60 | 53 |  | Age
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A | [6 empty] | Notes | N/A
Floor Construction, Secondary | Location | [6 empty] | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | Fair |  | 0.5 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A |  |  | N/A |  |  |  | Notes | N/A
Roof Construction, Structural Frame, Primary | Location | Typical |  |  | Typical |  |  | Site Lighting, Primary | Location | Typical
| Description | Wood, Beams and Joists |  |  | Concrete, CIP |  |  |  | Description | Pole Mounted H.I.D.
| Age | 60+ |  | 60 | 46 | 60 | 53 |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  | Condition | Good | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A | [6 empty] | Notes
Roof Construction, Structural Frame, Secondary | Location | [6 empty] | Site Lighting, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A |  |  | N/A |  |  |  | Notes | N/A
Exterior Walls / Exterior Assembly, Primary | Location | Typical |  |  | Typical |  |  | Playground Surface | Location | North
| Description | Brick, Solid (Mass) |  |  | Brick, Solid (Mass) |  |  |  | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 | 46 | 60 | 53 |  | Age | 30+ | 30
| Condition | Good |  | 0.75 | Fair |  | 0.5 |  | Condition | Poor | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A | [6 empty] | Notes
Exterior Walls / Exterior Assembly, Secondary | Location | [6 empty] | Playground Equipment | Location | North
| Description |  |  |  | Concrete, CIP |  |  |  | Description | B/Ball Backstops
| Age |  |  |  | 46 | 60 | 53 |  | Age | 30+ | 30
| Condition | Good |  | 0.75 | Very Poor |  | 0.1 |  | Condition | Poor | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A | [6 empty] | Notes
Exterior Windows, Primary | Location | Typical |  |  | Typical |  |  | TCUs | Location
| Description | Aluminum, Double Hung |  |  | Aluminum, Double Hung |  |  |  | Description
| Age | 16 | 21 | 18.5 | 30+ |  | 30 |  | Age
| Condition | Poor |  | 0.25 | Poor |  | 0.25 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | N/A | [6 empty] | Notes | N/A
Exterior Windows, Primary / Glazing | Location
| Description | Other (describe) |  |  | Glass, Single Pane
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Insulated glazing
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Security Grilles |  |  | Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary | Location
| Description |  |  |  | Aluminum, Double Hung
| Age |  |  |  | 30+ |  | 30
| Condition |  |  |  | Very Poor |  | 0.1
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | N/A
Exterior Windows, Secondary / Glazing | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
| CheckBox |  |  |  | Security Grilles / Other
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | Horizontal sun shading
Exterior Doors, Primary | Location | Typical |  |  | Typical
| Description | Steel (Hollow) |  |  | Steel (Hollow)
| Age | 31 | 45 | 38 | 31 | 45 | 38
| Condition | Poor |  | 0.25 | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location
| Description | Wood
| Age | 46 | 60 | 53
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | N/A
Roofing, Primary | Location | Roof |  |  | Roof
| Description | Asphalt Shingle |  |  | Polyurethane, Spray Applied
| Age | 22 | 30 | 26 | 41136 |  | 11.5
| Condition | Poor |  | 0.25 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Secondary | Location | Roof
| Description | Polyurethane, Spray Applied
| Age | 41136 |  | 11.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | N/A
Roof (Accessories) Supplementary Components / Flashing and Trim | Location | Roof |  |  | Roof
| Description | Aluminum |  |  | Aluminum
| Age | 41136 |  | 11.5 | 30+ |  | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location | Roof |  |  | Roof
| Description | Aluminum |  |  | Metal, Galvanized/Painted
| Age | 41136 |  | 11.5 | 30+ |  | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | N/A |  |  | N/A