## FCI Summary
Building Name: | EARLY COLLEGE H.S. | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 191950
Number of Floors: | B + 3
School Age (years): | 36
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 7.562%
Facility Condition = | GOOD
FCI Deficiency Cost = | 2993877.0106
FCI Replacement Cost = | 39589687.5
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 235
Historic 2005 LRFP Capacity = | NA
Adjusted 2012 Capacity = | 247
Recent Occupancy % = | 95.14%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 95.66%
Classroom Adequacy = | GOOD
Special Spaces Adequacy % Score = | 89.32%
Special Spaces Adequacy = | GOOD

## Uniformat FCI
Building Name: |  | EARLY COLLEGE H.S. | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 191950
Largest Floor Level Area: |  | 73392
Vertical FAR Ratio: |  | 2.6154
School Age (years): |  | 36
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 2.7% | 5.5687 | 191950 | 1068921.5625 | 100 | 36 | 64 | 0.5 | 50 | 100 | 1068921.5625 | 0 | 0%
|  |  | A1030 - SLAB ON GRADE | 2.65% | 5.4656 | 191950 | 1049126.7188 | 100 | 36 | 64 | 0.75 | 75 | 100 | 1049126.7188 | 0 | 0%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 191950 | 870973.125 | 100 | 36 | 64 | 0.75 | 75 | 100 | 870973.125 | 0 | 0%
|  |  | SUBTOTAL SUBSTRUCTURE | 7.55% | 15.5719 | 191950 | 2989021.4062
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 191950 | 4354865.625 | 100 | 36 | 64 | 0.75 | 75 | 100 | 4354865.625 | 0 | 0%
|  |  | B1020 - ROOF CONSTRUCTION | 3.4% | 7.0125 | 191950 | 1346049.375 | 100 | 36 | 64 | 0.75 | 75 | 100 | 1346049.375 | 0 | 0%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 7.7% | 15.8812 | 191950 | 3048405.9375 | 100 | 36 | 64 | 0.74342 | 74.3421 | 100 | 3048405.9375 | 0 | 0%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 4.4% | 9.075 | 191950 | 1741946.25 | 30 | 9.5 | 20.5 | 0.75 | 22.5 | 30 | 1741946.25 | 0 | 0%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 3% | 6.1875 | 191950 | 1187690.625 | 30 | 17.6667 | 12.3333 | 0.75 | 22.5 | 30 | 1187690.625 | 0 | 0%
|  |  | SUBTOTAL SHELL | 29.5% | 60.8438 | 191950 | 11678957.8125
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 191950 | 1583587.5 | 60 | 36 | 24 | 0.73077 | 43.8462 | 60 | 1583587.5 | 0 | 0%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 191950 | 593845.3125 | 20 | 21.697 | 0 | 0.51923 | 5 | 5 | 148461.3281 | 445383.9844 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 191950 | 1583587.5 | 20 | 15.125 | 4.875 | 0.6875 | 13.75 | 18.625 | 1474715.8594 | 108871.6406 | 6.875%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 191950 | 593845.3125 | 30 | 36 | 0 | 0.5 | 5 | 5 | 98974.2188 | 494871.0938 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 3.2% | 6.6 | 191950 | 1266870 | 10 | 6.2985 | 3.7015 | 0.62121 | 6.2121 | 9.9136 | 1255925.9851 | 10944.0149 | 0.8639%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 191950 | 2375381.25 | 20 | 17.6838 | 2.3162 | 0.56136 | 11.2273 | 13.5434 | 1608542.7642 | 766838.4858 | 32.28%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 191950 | 2375381.25 | 30 | 18.8175 | 11.1825 | 0.51613 | 15.4839 | 26.6664 | 2111429.7288 | 263951.5212 | 11.11%
|  |  | SUBTOTAL INTERIORS | 26.2% | 54.0375 | 191950 | 10372498.125
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 0.75% | 1.5469 | 191950 | 296922.6562 | 60 | NA | 0 | 0.1 | 0 | 0 | 0 | 296922.6562 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 191950 | 593845.3125 | 60 | 26.707 | 33.293 | 0.586 | 35.1597 | 60 | 593845.3125 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 191950 | 514665.9375 | 60 | 11.5 | 48.5 | 0.75 | 45 | 60 | 514665.9375 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 191950 | 475076.25 | 60 | 36 | 24 | 0.5 | 30 | 54 | 427568.625 | 47507.625 | 10%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 191950 | 197948.4375 | 30 | 36 | 0 | 0.5 | 5 | 5 | 32991.4062 | 164957.0312 | 83.33%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 2.7% | 5.5687 | 191950 | 1068921.5625 | 60 | 21.5 | 38.5 | 0.5 | 30 | 60 | 1068921.5625 | 0 | 0%
|  |  | D3020 - BOILERS | 2% | 4.125 | 191950 | 791793.75 | 60 | 22.75 | 37.25 | 0.5 | 30 | 60 | 791793.75 | 0 | 0%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4% | 8.25 | 191950 | 1583587.5 | 40 | 16.625 | 23.375 | 0.5625 | 22.5 | 40 | 1583587.5 | 0 | 0%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4% | 8.25 | 191950 | 1583587.5 | 40 | 20.1786 | 19.8214 | 0.55138 | 22.0551 | 40 | 1583587.5 | 0 | 0%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 2% | 4.125 | 191950 | 791793.75 | 40 | 0 | 40 | 0 | 0 | 40 | 791793.75 | 0 | 0%
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.5% | 3.0938 | 191950 | 593845.3125 | 20 | 0 | 20 | 0 | 0 | 20 | 593845.3125 | 0 | 100%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 191950 | 395896.875 | 20 | 0 | 20 | 0 | 0 | 20 | 395896.875 | 0 | 0%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 191950 | 79179.375 | 20 | 10 | 10 | 0.75 | 15 | 20 | 79179.375 | 0 | 0%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 191950 | 514665.9375 | 60 | 36 | 24 | 0.5 | 30 | 54 | 463199.3438 | 51466.5938 | 10%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 191950 | 2771278.125 | 30 | 17.773 | 12.227 | 0.72807 | 21.8421 | 30 | 2771278.125 | 0 | 0%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 191950 | 1187690.625 | 20 | 12.5863 | 7.4137 | 0.61746 | 12.3493 | 19.763 | 1173616.1207 | 14074.5043 | 1.185%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 191950 | 118769.0625 | 20 | 18.3621 | 1.6379 | 0.6557 | 13.114 | 14.752 | 87603.8593 | 31165.2032 | 26.24%
|  |  | SUBTOTAL SERVICES | 34.25% | 70.6406 | 191950 | 13559467.9688
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 191950
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 191950
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 191950
|  |  | E1090 - OTHER EQUIPMENT |  |  | 191950
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 191950
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 191950
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 191950
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 191950
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 191950
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 191950 | 395896.875 | 30 | 30 | 0 | 0.5 | 15 | 15 | 197948.4375 | 197948.4375 | 50%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 191950 | 197948.4375 | 30 | 30 | 0 | 0.5 | 15 | 15 | 98974.2188 | 98974.2188 | 50%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 191950 | 197948.4375 | 30 | 18.5 | 11.5 | 0.75 | 22.5 | 30 | 197948.4375 | 0 | 0%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 191950 | 197948.4375 | 30 | 11.5 | 18.5 | 0.75 | 22.5 | 30 | 197948.4375 | 0 | 0%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 191950 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 191950
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 191950 | 39589687.5 | [7 empty] | 2993877.0106 | 7.562%
100%

## Master File (Interior)
Louise A. Spencer
School Code:
NPS Code:
Street: | 66 Muhammad Ali Blvd.
City/Town: | Newark,
Database ID: | 35
Total size (gsf):
ROOM INFORMATION | [12 empty] | 36.6207 | Ave Condition | 0.73684 | [6 empty] | 17.6838 | Ave Condition | 0.56136 | [6 empty] | 6.2985 | Ave Condition | 0.62121 | [6 empty] | 18.8175 | Ave Condition | 0.51613 | [6 empty] | 21.697 | Ave Condition | 0.51923 | [6 empty] | 37.1515 | Ave Condition | 0.73077 | [6 empty] | 27.6667 | Ave Condition | 0.55556 | [5 empty] | 30 | Ave Condition | 0.51786 | [5 empty] | 28.3182 | Ave Condition | 0.54545 | [5 empty] | 30 | Ave Condition | 0.61111 | [6 empty] | 17.55 | Ave Condition | 0.7 | [6 empty] | 15.125 | Ave Condition | 0.6875 | [5 empty] | 11.819 | Ave Condition | 0.68421 | [6 empty] | 29.2241 | Ave Condition | 0.5614 | [5 empty] | 30 | Ave Condition | 0.49561 | [6 empty] | 10.3571 | Ave Condition | 0.60714 | [6 empty] | 10 | Ave Condition | 0.75 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [6 empty] | 1.5 | Ave Condition | 0.75 | [5 empty] | Average Age | 9.6216 | Ave Condition | 0.52703 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [7 empty] | Plumbing Fixtures - Urinals | [7 empty] | Plumbing Fixtures - Showers | [7 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [7 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
12024 | 1 | Conference Room | 1st Floor | A | Administration |  |  | 956 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12025 | 2 | Training Center | 1st Floor | A | Administration |  |  | 1653 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12026 | 3 | Conference Room | 1st Floor | A | Administration |  |  | 1110 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12027 | 4 | Office | 1st Floor | A | Administration |  |  | 1629 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12028 | 5 | Conference Room | 1st Floor | A | Administration |  |  | 2222 | 10' 3" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Tectum | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Good | 0.75 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | 0 | [17 empty] | 0 | Present | [10 empty] | Wireless (WiFi) | 0 | 3 | 1.5 | Good | 0.75 | [117 empty] | 0 | Present
12029 | 113 | Security | 1st Floor | A | Administration |  |  | 90 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12030 | 114 | Home Economics | 1st Floor | A | Technological Literacy |  |  | 1109 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | 5 | [44 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present
12031 | UN-1 | N/A | 1st Floor | A | N/A |  |  | 2054 | N/A
12032 | UN-2 | Storage | 1st Floor | A | Administration |  |  | 38 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12033 | UN-3 | Custodial Closet | 1st Floor | A | Support |  |  | 31 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12034 | UN-4 | Mens' Water Closet | 1st Floor | A | Faculty Support |  |  | 143 | 9' 2" | [9 empty] | Epoxy | [17 empty] | Plaster | [32 empty] | 2 | [7 empty] | 2 | [7 empty] | 0
12035 | UN-5 | Womens' Water Closet | 1st Floor | A | Faculty Support |  |  | 159 | 9' 2" | [9 empty] | Epoxy | [17 empty] | Plaster | [32 empty] | 2 | [7 empty] | 2 | [7 empty] | 0
12036 | UN-6 | Office | 1st Floor | A | Administration |  |  | 937 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12037 | UN-7 | Office | 1st Floor | A | Administration |  |  | 221 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12038 | UN-8 | Storage | 1st Floor | A | Administration |  |  | 46 | 10' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12039 | UN-9 | Girls' Water Closet | 1st Floor | A | Support |  |  | 179 | 7' 9" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [32 empty] | 2 | [7 empty] | 2 | [7 empty] | 0
12040 | UN-10 | Boys' Water Closet | 1st Floor | A | Support |  |  | 188 | 7' 9" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [32 empty] | 2 | [7 empty] | 2 | [7 empty] | 2
12041 | UN-11 | N/A | 1st Floor | A | N/A |  |  | 200 | N/A
12042 | UN-12 | Boiler Room | 1st Floor | A | Support |  |  | 772 | 15' 10" | [9 empty] | Unfinished | [17 empty] | Acoustical Panel
12043 | UN-13 | Mechanical Equipment | 1st Floor | A | Support |  |  | 4654 | 15' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
12044 | UN-14 | Woodshop | 1st Floor | A | Technological Literacy |  |  | 1607 | 11' | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Metal/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Poor | 0.25 | 1 |  | And drinking fountain | [42 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [11 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [10 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [108 empty] | Present - Present
12045 | UN-15 | Storage | 1st Floor | A | Support |  |  | 291 | N/A | [9 empty] | Solid Terrazzo
12046 | UN-16 | Parent Center | 1st Floor | A | Administration |  |  | 1926 | 11' | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wood | 41070 |  | 8 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | 1 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | [19 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | [7 empty] | 10 CPUs | [106 empty] | Present - Present - Present
12047 | UN-17 | Storage | 1st Floor | A | Technological Literacy |  |  | 122 | N/A
12048 | UN-18 | Storage | 1st Floor | A | Technological Literacy |  |  | 107 | N/A
12049 | UN-19 | Storage | 1st Floor | A | Technological Literacy |  |  | 110 | N/A
12050 | UN-20 | N/A | 1st Floor | A | Technological Literacy |  |  | 79 | N/A
12051 | UN-21 | Womens' Water Closet | 1st Floor | A | Faculty Support |  |  | 260 | 9' 4" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [32 empty] | 5 | [7 empty] | 3 | [7 empty] | 0
12052 | UN-22 | Custodial Closet | 1st Floor | A | Support |  |  | 40 | 9' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
12053 | UN-23 | Mens' Water Closet | 1st Floor | A | Faculty Support |  |  | 279 | 9' 4" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [32 empty] | 3 | [7 empty] | 2 | [7 empty] | 5
12054 | UN-24 | Student Lounge | 1st Floor | A | Assembly/Large Group (9-12) |  |  | 1302 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Suspended Acoustical
12055 | UN-25 | N/A | 1st Floor | A | N/A |  |  | 155 | N/A
12056 | UN-26 | N/A | 1st Floor | A | N/A |  |  | 129 | N/A
12057 | UN-27 | Home Economics | 1st Floor | A | Technological Literacy |  |  | 1300 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12058 | UN-28 | N/A | 1st Floor | A | Technological Literacy |  |  | 88 | N/A
12059 | UN-29 | N/A | 1st Floor | A | Technological Literacy |  |  | 92 | N/A
12060 | UN-30 | N/A | 1st Floor | A | Technological Literacy |  |  | 111 | N/A
12061 | UN-31 | Art | 1st Floor | A | Visual & Performing Arts |  |  | 1444 | 11' | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 3 | [106 empty] | Present - Present - Present - Present
12062 | UN-32 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 184 | 9' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
12063 | UN-33 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 150 | 9' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
12064 | UN-34 | N/A | 1st Floor | A | N/A |  |  | 171 | N/A
12065 | UN-35 | N/A | 1st Floor | A | N/A |  |  | 174 | N/A
12066 | UN-36 | N/A | 1st Floor | A | N/A |  |  | 172 | N/A
12067 | UN-37 | Music Room | 1st Floor | A | Visual & Performing Arts |  |  | 730 | 9' 9" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12068 | UN-38 | N/A | 1st Floor | A | Visual & Performing Arts |  |  | 73 | N/A
12069 | UN-39 | N/A | 1st Floor | A | Visual & Performing Arts |  |  | 51 | N/A
12070 | UN-40 | Girls' Water Closet | 1st Floor | A | Support |  |  | 183 | 9' 4" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 4 | [7 empty] | 4 | [7 empty] | 0
12071 | UN-41 | Custodial Closet | 1st Floor | A | Support |  |  | 59 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12072 | UN-42 | Boys' Water Closet | 1st Floor | A | Support |  |  | 224 | 9' 4" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 4 | [7 empty] | 4 | [7 empty] | 4
12073 | UN-43 | Gym | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 6423 | 17'10 | CMU Back-up Wall | 31 | 45 | 38 |  |  | 0 |  |  | Wood | 20+ |  | 20 |  |  | 0 |  |  | Painted Walls | 41004 |  | 4.5 |  |  | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 |  |  | 0 |  |  | Metal/Metal Frame | 20+ |  | 20 |  |  | 0 |  |  | Concrete Block | 31 | 45 | 38 |  |  | 0 | [32 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 |  |  | 0 |  |  | Keyed Wall Switches | 30+ |  | 30 |  |  | 0 |  |  | Other (describe) | 30+ | 30 |  |  | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12074 | UN-44 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 124 | N/A
12075 | UN-45 | Office | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 126 | 9' 6" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wood | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 |  |  | tectum | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Fair | 0.5 | [9 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [10 empty] | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | ducted air diffusers | [25 empty] | Present | [43 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present
12076 | UN-46 | Girl\'s Locker Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 876 | 9' 6" | [9 empty] | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Metal/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 3 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 3 | [10 empty] | Compartmental Showers | 30+ | 30 | Poor | 0.25 | 0 | [11 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | 0 | [5 empty] | Fair | 0.5 | 0 |  | Central hv | [24 empty] | 0 | Present - Present - Present - Present - Present
12077 | UN-47 | Boy's Locker Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 802 | 9' 6" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel
12078 | UN-48 | Office | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 125 | 9' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12079 | UN-49 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 120 | N/A
12080 | UN-50 | Cafeteria | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 10183 | 12' | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Demountable/Folding. | 31 | 45 | 38 | Fair | 0.5 | [9 empty] | 0 | [26 empty] | Wall Mounted Electric Water Coolers | 0 | 7 | 3.5 | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | ducted air diffusers | [25 empty] | Present - Present | [35 empty] | Present | [98 empty] | Present - Present | [35 empty] | Present
12081 | UN-51 | Kitchen | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 2138 | 10' | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Ceramic Tile | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Stainless Steel Sinks | 30+ |  | 30 | Good | 0.75 | 5 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | ducted air diffusers | [9 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [10 empty] | Present - Present - Present | [161 empty] | Present | [8 empty] | Present - Present
12082 | UN-52 | Serving | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 557 | 10' | [9 empty] | Ceramic Tile | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Good | 0.75 | 1 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 | 0 |  | ducted air diffusers | [9 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [9 empty] | 0 | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 41100 |  | 8.5 | Good | 0.75 | 0 |  | 2 cpu | [132 empty] | 0 | Present - Present | [7 empty] | 0 | Present - Present - Present
12083 | UN-53 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 219 | 10' | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel
12084 | UN-54 | Freezer | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 77 | N/A
12085 | UN-55 | Custodian Room | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 154 | 10' | [9 empty] | Ceramic Tile | [17 empty] | Plaster
12086 | UN-56 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 438 | 10' | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel
12087 | UN-57 | Freezer | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 224 | N/A
12088 | UN-58 | Serving | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 548 | 10' | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel
12089 | UN-59 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 149 | 10' | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel
12090 | UN-60 | Office | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 69 | 10' | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel
12091 | UN-61 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 78 | N/A
12092 | UN-62 | Mens\' Water Closet | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 89 | 8' | [9 empty] | Ceramic Tile | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 |  |  |  | Suspended Acoustical | 22 | 30 | 26 | Poor | 0.25 | 0 |  | water damage | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [7 empty] | 1 | [7 empty] | 1 | [28 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | exhaust vent | [25 empty] | Present - Present - Present - Present - Present
12093 | UN-63 | Custodian Closet | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 26 | 8' | [9 empty] | Unfinished | [17 empty] | Acoustical Panel
12094 | UN-64 | Womens' Water Closet | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 98 | 8' | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [32 empty] | 2 | [7 empty] | 2 | [7 empty] | 0
12095 | UN-65 | Locker Room | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 129 | 8' | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel
12096 | UN-66 | Music Room | 1st Floor | A | Visual & Performing Arts |  |  | 890 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | concealed spline | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  | acoustically treated | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 0 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | ducted air diffusers | [25 empty] | Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 41100 |  | 8.5 | Good | 0.75 | [109 empty] | Present - Present - Present
12097 | UN-67 | N/A | 1st Floor | A | Visual & Performing Arts |  |  | 121 | N/A
12098 | UN-68 | Auditorium | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 10649 | 23' | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 |  |  | acoustic wood panels | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [9 empty] | 0 | [44 empty] | Fluorescent Recessed Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Good | 0.75 |  |  | ducted air diffusers | [160 empty] | Present - Present - Present - Present
12099 | UN-69 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 118 | N/A
12100 | UN-70 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 118 | N/A
12101 | UN-71 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 153 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 22 | 30 | 26 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [9 empty] | 0 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | exhaust chase | [25 empty] | Present - Present - Present - Present - Present - Present - Present
12102 | UN-72 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 189 | N/A
12103 | UN-73 | N/A | 1st Floor | A | N/A |  |  | 95 | N/A
12104 | UN-74 | N/A | 1st Floor | A | N/A |  |  | 98 | N/A
12105 | UN-75 | N/A | 1st Floor | A | Administration |  |  | 99 | N/A
12106 | UN-76 | N/A | 1st Floor | A | Administration |  |  | 94 | N/A
12107 | UN-77 | N/A | 1st Floor | A | Administration |  |  | 87 | N/A
12108 | 203 | Community Office | 2nd Floor | A | Administration |  |  | 716 | 9' 3" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Carpet | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  | Perimeter water damage at window | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Stainless Steel Sinks | 30+ |  | 30 | Poor | 0.25 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 |  |  | Central hv | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 6 CPUs
12109 | 207 | Office | 2nd Floor | A | Administration |  |  | 819 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12110 | 209 | Multi Purpose Room A | 2nd Floor | A | Small Group Instruction |  |  | 990 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | [19 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 CPU and several laptop ethernet connections | [106 empty] | Present
12111 | 211 | Multi Purpose Room B | 2nd Floor | A | Food Service/Assembly (K-8) |  |  | 875 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12112 | 213 | Resource Tech Coordinators | 2nd Floor | A | Administration |  |  | 794 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Carpet | 16 | 20 | 18 | Poor | 0.25 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | [19 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 4 | [106 empty] | Present - Present
12113 | 215 | Special Education | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 791 | 9' 4" | [9 empty] | Carpet | [17 empty] | Acoustical Panel
12114 | 216 | Special Education | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 887 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12115 | 217 | 1st Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 792 | 9' 4" | [9 empty] | Carpet | [17 empty] | Acoustical Panel
12116 | 219 | Special Education | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 806 | 9' 4 | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Very Good | 0.9 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 10 | [72 empty] | Present - Present - Present
12117 | 220 | Kindergarten | 2nd Floor | A | Kindergarten Classroom |  |  | 903 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12118 | 221 | Special Ed | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 785 | 9' 4" | [9 empty] | Carpet | [17 empty] | Acoustical Panel
12119 | 222 | Special Ed (Autistic Grade PSD) | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 878 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Very Good | 0.9 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present - Present - Present
12120 | 223 | Pre-K | 2nd Floor | A | Kindergarten Classroom |  |  | 842 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | [50 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [47 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [71 empty] | 0 | Present - Present - Present - Present - Present
12121 | 224 | Computer Lab | 2nd Floor | A | Technological Literacy |  |  | 792 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Carpet | 16 | 20 | 18 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 2 | [17 empty] | 17 | [72 empty] | Present - Present - Present - Present - Present - Present
12122 | 225 | 1st Grade Special Education | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 856 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
12123 | 226 | 2nd Grade Special Eduaction | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 778 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  | Portable floor mounted | [6 empty] | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [26 empty] | 3 | [71 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
12124 | 227 | Kindergarten | 2nd Floor | A | Kindergarten Classroom |  |  | 865 | 9' 4" | [9 empty] | Carpet | [17 empty] | Acoustical Panel
12125 | 228 | 2nd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 772 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12126 | 229 | Kindergarten | 2nd Floor | A | Kindergarten Classroom |  |  | 806 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [24 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [26 empty] | 3 | [71 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
12127 | 230 | 1st Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 795 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [47 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [71 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
12128 | 231 | 2nd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 908 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12129 | 232 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 770 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12130 | 233 | 2nd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 781 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [26 empty] | 3 | [71 empty] | 0
12131 | 234 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 653 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12132 | 235 | 1st Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 794 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12133 | 237 | 1st Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 789 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12134 | 239 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 819 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12135 | 241 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 1039 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [26 empty] | 3 | [71 empty] | 0
12136 | UN-78 | Offices | 2nd Floor | A | Administration |  |  | 2009 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Carpet | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 6 CPUs | [6 empty] | 0 | [98 empty] | 0
12137 | UN-79 | Storage | 2nd Floor | A | Support |  |  | 98 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12138 | UN-80 | Storage | 2nd Floor | A | Administration |  |  | 118 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12139 | UN-81 | Speech Therapy | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 303 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12140 | UN-82 | Storage | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 36 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12141 | UN-83 | Womens' Water Closet | 2nd Floor | A | Faculty Support |  |  | 174 | 8' 7" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Sheet Vinyl | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Fair | 0.5 | 0 |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 2 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 2 | [7 empty] | 0 | [16 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12142 | UN-84 | Mens' Water Closet | 2nd Floor | A | Faculty Support |  |  | 167 | 8' 7" | [9 empty] | Epoxy | [17 empty] | Acoustical Panel | [32 empty] | 2 | [7 empty] | 2 | [7 empty] | 1
12143 | UN-85 | Custodial Closet | 2nd Floor | A | Support |  |  | 29 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12144 | UN-86 | General Office | 2nd Floor | A | Administration |  |  | 872 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  | Central hv | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 2 CPU | [6 empty] | 0 | [98 empty] | 0 |  | Headend paging control
12145 | UN-87 | Storage | 2nd Floor | A | Administration |  |  | 127 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12146 | UN-88 | Copy Room | 2nd Floor | A | Administration |  |  | 356 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12147 | UN-89 | Storage | 2nd Floor | A | Administration |  |  | 204 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12148 | UN-90 | Principal's Office | 2nd Floor | A | Administration |  |  | 446 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  | and central hv | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | IDF 2. 1 CPU | [6 empty] | 0 | [98 empty] | 0
12149 | UN-91 | Storage | 2nd Floor | A | Administration |  |  | 63 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12150 | UN-92 | Water Closet | 2nd Floor | A | Administration |  |  | 33 | 8' | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
12151 | UN-93 | Conference Room | 2nd Floor | A | Administration |  |  | 367 | 9' 4" | [15 empty] | 0 | [17 empty] | 0
12152 | UN-94 | Nurse | 2nd Floor | A | Health Services |  |  | 595 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 16 | 21 | 18.5 | Good | 0.75 | [33 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 CPU | [6 empty] | 0 | [98 empty] | 0
12153 | UN-95 | Exam Room | 2nd Floor | A | Health Services |  |  | 88 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Some water damage | Wood Fire/Metal Frames | 20+ |  | 20 | Poor | 0.25 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 16 | 21 | 18.5 | Good | 0.75 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | Central hv | [45 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5
12154 | UN-96 | Storage | 2nd Floor | A | Health Services |  |  | 63 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12155 | UN-97 | Water Closet | 2nd Floor | A | Health Services |  |  | 30 | 8' | [9 empty] | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 1 | [7 empty] | 0 | [28 empty] | Fluorescent Recessed Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | Central hv
12156 | UN-98 | Exam Room | 2nd Floor | A | Health Services |  |  | 98 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [41 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12157 | UN-99 | N/A | 2nd Floor | A | N/A |  |  | 134 | N/A
12158 | UN-100 | Vault | 2nd Floor | A | Administration |  |  | 132 | N/A
12159 | UN-101 | Water Closet | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 45 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12160 | UN-102 | Water Closet | 2nd Floor | A | Kindergarten Classroom |  |  | 45 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12161 | UN-103 | Water Closet | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 49 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12162 | UN-104 | Water Closet | 2nd Floor | A | Technological Literacy |  |  | 43 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12163 | UN-105 | Water Closet | 2nd Floor | A | Kindergarten Classroom |  |  | 36 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12164 | UN-106 | Water Closet | 2nd Floor | A | Support |  |  | 45 | 7'8 | [6 empty] | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Drywall (Gypsum) | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [8 empty] | 0 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 2 | [7 empty] | 0 | [16 empty] | 0 |  |  | Metal, Powder Coated | 31 | 45 | 38 | Fair | 0.5 | 0 |  |  | Fluorescent Recessed Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 | 0 |  | Toilet exhaust vent | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12165 | UN-107 | Water Closet | 2nd Floor | A | Kindergarten Classroom |  |  | 39 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12166 | UN-108 | Water Closet | 2nd Floor | A | Kindergarten Classroom |  |  | 46 | 7'8 | [6 empty] | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Drywall (Gypsum) | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [8 empty] | 0 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 2 | [7 empty] | 0 | [7 empty] | 0 | [8 empty] | 0 |  |  | Metal, Powder Coated | 31 | 45 | 38 | Fair | 0.5 | 0 |  |  | Fluorescent Recessed Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 | 0 |  | Toilet exhaust vent | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12167 | UN-109 | Custodial Closet | 2nd Floor | A | Support |  |  | 36 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster
12168 | UN-110 | N/A | 2nd Floor | A | N/A |  |  | 261 | N/A
12169 | UN-111 | N/A | 2nd Floor | A | N/A |  |  | 330 | N/A
12170 | UN-112 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 269 | 8' 8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 3 | [7 empty] | 2 | [7 empty] | 5
12171 | UN-113 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 276 | 8' 8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 5 | [7 empty] | 4 | [7 empty] | 0
12172 | UN-114 | Custodial Closet | 2nd Floor | A | Support |  |  | 37 | 9' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
12173 | UN-115 | Mens' Water Closet | 2nd Floor | A | Faculty Support |  |  | 64 | 8' 8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 1 | [7 empty] | 1 | [7 empty] | 1
12174 | UN-116 | Womens' Water Closet | 2nd Floor | A | Faculty Support |  |  | 47 | 8' 8" | [6 empty] | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 1 | [7 empty] | 0 | [16 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Lay-In Fixture (Troffer) | 30+ | 30 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 | 0 |  | Toilet exhaust vent | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12175 | UN-117 | Teachers' Lounge | 2nd Floor | A | Faculty Support |  |  | 520 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [33 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wet Chemical | 16 | 21 | 18.5 | Good | 0.75 | 0 |  | Water class 2a | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12176 | UN-118 | Water Closet | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 45 | 7' 8" | [15 empty] | 0 | [17 empty] | 0 | [26 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12177 | UN-119 | Water Closet | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 42 | 7'8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 0 | [7 empty] | 2 | [7 empty] | 0
12178 | UN-120 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 257 | 8' 8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 3 | [7 empty] | 3 | [7 empty] | 6
12179 | UN-121 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 255 | 8' 8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 5 | [7 empty] | 5 | [7 empty] | 0
12180 | UN-122 | Custodial Closet | 2nd Floor | A | Support |  |  | 31 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12181 | 302 | 4th Grade Special Education | 3rd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 796 | 9' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12182 | 303 | 4th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 854 | 9' 8" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [47 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [71 empty] | 0 | Present
12183 | 304 | Math Coach/ Literacy Coach | 3rd Floor | A | Small Group Instruction |  |  | 822 | 9' 8" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Poor | 0.25 | 0 |  | Exterior wall water damage | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [27 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 | [72 empty] | Present - Present
12184 | 305 | 3rd Grade Classroom | 3rd Floor | A | General Classroom (Grades 1-3) |  |  | 902 | 9' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12185 | 306 | 4th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 806 | 9' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12186 | 307 | 4th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 855 | 9' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12187 | 308 | MD | 3rd Floor | A | Administration |  |  | 759 | 9' 8" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | [28 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 3 CPUs | [106 empty] | Present - Present - Present
12188 | 309 | 3rd Grade Classroom | 3rd Floor | A | General Classroom (Grades 1-3) |  |  | 855 | 9' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12189 | 310 | LLD-M | 3rd Floor | A | Administration |  |  | 808 | 9' 8" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 41004 |  | 4.5 | Good | 0.75 |  |  | 3 CPUs | [106 empty] | Present - Present - Present - Present
12190 | 311 | 3rd Grade Classroom | 3rd Floor | A | General Classroom (Grades 1-3) |  |  | 759 | 9' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12191 | 313 | Library | 3rd Floor | A | Media Center |  |  | 2184 | 9' 7" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Carpet | 16 | 20 | 18 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | [19 empty] | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 6 | [17 empty] | 5 | [72 empty] | Present - Present - Present - Present - Present
12192 | 315 | ESL Room | 3rd Floor | A | Small Group Instruction |  |  | 822 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 |  | Wall mounted. Plus 6 portable smartboards | [15 empty] | 3 | [72 empty] | Present - Present - Present - Present - Present - Present
12193 | 316 | N/A | 3rd Floor | A | N/A |  |  | 261 | N/A
12194 | 317 | ESL Room | 3rd Floor | A | Small Group Instruction |  |  | 823 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12195 | 318 | Book Storage | 3rd Floor | A | Support |  |  | 345 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12196 | 319 | Vice Principal | 3rd Floor | A | Administration |  |  | 837 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 |  |  | 1 CPU | [106 empty] | Present - Present - Present - Present - Present - Present - Present
12197 | 320 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 745 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
12198 | 321 | Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 814 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 2 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
12199 | 323 | 4th Grade Special Eduaction | 3rd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 837 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Good | 0.75 | 0 | [17 empty] | 1 |  | Wall mounted | [15 empty] | 3 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
12200 | 324 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 768 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12201 | 325 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 820 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12202 | 326 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 755 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12203 | 327 | 5th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 910 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 |  | Wall mounted | [15 empty] | 3 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
12204 | 328 | 5th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 757 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12205 | 329 | 5th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 888 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12206 | 330 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 757 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12207 | 331 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 951 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12208 | 332 | 6th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 891 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12209 | 333 | 6th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 823 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12210 | 334 | 6th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 784 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12211 | 335 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 832 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | [19 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
12212 | 336 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 790 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12213 | 337 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 820 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12214 | 338 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 759 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12215 | 339 | 6th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 851 | 9' 4 | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0
12216 | 340 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 653 | 9' 4" | [15 empty] | 0 | [17 empty] | 0
12217 | 341 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 828 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12218 | 342 | Computer Room | 3rd Floor | A | Technological Literacy |  |  | 1101 | 9' 4" | CMU Back-up Wall | 31 | 45 | 38 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0
12219 | 343 | Vault | 3rd Floor | A | Administration |  |  | 226 | N/A
12220 | 344 | Office | 3rd Floor | A | Administration |  |  | 287 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12221 | 345 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 925 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12222 | 346 | N/A | 3rd Floor | A | N/A |  |  | 259 | N/A
12223 | UN-123 | Small Group Instruction | 3rd Floor | A | Small Group Instruction |  |  | 232 | 9' 8" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 | [53 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0
12224 | UN-124 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 266 | 9' 9" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 4 | [7 empty] | 3 | [7 empty] | 5
12225 | UN-125 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 280 | 9' 9" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 6 | [7 empty] | 6 | [7 empty] | 0
12226 | UN-126 | Custodial Closet | 3rd Floor | A | Support |  |  | 42 | 9' 9" | [9 empty] | Unfinished | [17 empty] | Plaster
12227 | UN-127 | N/A | 3rd Floor | A | Media Center |  |  | 340 | N/A
12228 | UN-128 | Office | 3rd Floor | A | Media Center |  |  | 304 | 9' 7" | [9 empty] | Carpet | [17 empty] | Acoustical Panel
12229 | UN-129 | N/A | 3rd Floor | A | N/A |  |  | 134 | N/A
12230 | UN-130 | Book Storage | 3rd Floor | A | Support |  |  | 132 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12231 | UN-131 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 255 | 9' 2" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Drywall (Gypsum) | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 4 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 3 |  |  | Wall Hung | 30+ | 30 | Fair | 0.5 | 6 | [16 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Poor | 0.25 | 0 |  | Toilet exhaust | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12232 | UN-132 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 277 | 9' 3" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 6 | [7 empty] | 5 | [7 empty] | 0
12233 | UN-133 | Custodial Closet | 3rd Floor | A | Support |  |  | 37 | 9' 4" | [9 empty] | Ceramic Tile | [17 empty] | Plaster
12234 | UN-134 | Mens' Water Closet | 3rd Floor | A | Faculty Support |  |  | 64 | 7' 9" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [32 empty] | 1 | [7 empty] | 1 | [7 empty] | 1
12235 | UN-135 | Teachers' Lounge | 3rd Floor | A | Faculty Support |  |  | 520 | 9' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
12236 | UN-136 | Womens' Water Closet | 3rd Floor | A | Faculty Support |  |  | 47 | 7' 9" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [32 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
12237 | UN-137 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 257 | 9' 3" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Drywall (Gypsum) | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 4 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 3 |  |  | Wall Hung | 30+ | 30 | Fair | 0.5 | 5 | [16 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Poor | 0.25 | 0 |  | Toilet exhaust | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12238 | UN-138 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 255 | 9' 3" | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Drywall (Gypsum) | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 4 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 6 | [7 empty] | 0 | [16 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  | Toilet exhaust | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
12239 | UN-139 | Custodial Closet | 3rd Floor | A | Support |  |  | 31 | 9' 3" | [9 empty] | Ceramic Tile | [17 empty] | Plaster
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [7 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
37 | A |  | 2nd floor | [6 empty] | Other (describe) | 31 | 45 | 38 | Good | 0.75 |  |  | Brick | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Other (describe) | 10+ |  | 10 | Good | 0.75 |  |  | Brick | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Other (describe) | 31 | 45 | 38 | Good | 0.75 |  |  | Brick | [9 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ | 30 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ | 30 | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ | 30 | Good | 0.75 | [19 empty] | Present | [17 empty] | Monitor | [6 empty] | Present
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [7 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
120 | A |  | 1st floor | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | [12 empty] | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [21 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ | 30 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ | 30 | Good | 0.75 |  |  |  | Wet Chemical | 0 | 7 | 3.5 | Good | 0.75 |  |  | Water | [7 empty] | Present | [16 empty] | Present | [7 empty] | Present
121 | B |  | 2nd floor | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 30+ | 30 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ | 30 | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ | 30 | Good | 0.75 |  |  |  | Wet Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present | [16 empty] | Present | [7 empty] | Present
122 | C |  | 2nd floor | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Good | 0.75 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ | 30 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Good | 0.75 | [11 empty] | Wet Chemical | 0 | 7 | 3.5 | Good | 0.75 |  |  | Water | [7 empty] | Present | [16 empty] | Present | [7 empty] | Present
123 | D |  | 3rd floor | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ | 30 | Poor | 0.25 |  |  |  | Keyed Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Fin Tube Radiation | 30+ | 30 | Poor | 0.25 |  |  |  | Wet Chemical | 41136 |  | 11.5 | Good | 0.75 |  |  | Water type | [7 empty] | Present | [16 empty] | Present | [7 empty] | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [7 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [7 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
114 | A |  | 1st-3rd | [6 empty] | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Steel Pan | 30+ |  | 30 | [5 empty] | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Natural Stone | 30+ |  | 30 | Good | 0.75 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 30+ | 30 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ | 30 | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [18 empty] | Present
115 | B |  | 1st-3rd | [6 empty] | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Steel Pan | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Natural Stone | 30+ |  | 30 | Good | 0.75 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 30+ | 30 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ | 30 | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Good | 0.75 | [18 empty] | Present
116 | C |  | 1st-3rd | [6 empty] | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Steel Pan | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Natural Stone | 30+ |  | 30 | Good | 0.75 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 30+ | 30 | Poor | 0.25 |  |  |  | Keyed Wall Switches | 30+ | 30 | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Good | 0.75 | [18 empty] | Present
117 | D |  | 1st-3rd | [6 empty] | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Steel Pan | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Natural Stone | 30+ |  | 30 | Good | 0.75 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Good | 0.75 | [18 empty] | Present
Elevators | [9 empty] | Elevator | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Car Load Capacity | [7 empty] | Elevator Equipment and Controls
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
13 | A |  | Basement - 3rd floor | [6 empty] | Hydraulic | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Fluorescent Lay-In Fixture (Troffer) | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [7 empty] | 0 |  | 3000 lbs | [5 empty] | 0

## Master File (Systems)
systems | Question | Value1 |  | Average1 | systems | Question | Value1 | Average1
Systems | Seg ID | 922 |  |  | InfoTech | Seg ID | 361
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 0 |  |  |  | Addition | 0
| Year Built | 1976 |  |  |  | Year Built | 1976
Domestic Water Heaters | Location | un13 |  |  | Entrance Facilities (Demarc or Cable Vault) | Location
| Description | Fuel/Fired Water Heater |  |  |  | Description
| Age | 41136 |  | 11.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Sanitary Drainage | Location | roof |  |  | Main Dist. Facility (MDF) | Location | Above Ground Level Floor
| Description | Other (describe) |  |  |  | Description | floor mounted rack
| Age | 31 | 45 | 38 |  | Age | 41100 | 8.5
| Condition | Fair |  | 0.5 |  | Condition | Good | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | exhaust vents |  |  |  | Notes | room 342
Building Support (other) Plumbing Systems | Location | roof |  |  | MDF, HVAC Terminal Units | Location
| Description | Stormwater Area Drains |  |  |  | Description | Fin Tube Radiation
| Age | 31 | 45 | 38 |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Piping | Location | un13 |  |  | MDF, Packaged Terminal Air Conditioner | Location
| Description | Gas Piping |  |  |  | Description | Window Mounted
| Age | 0 | 15 | 7.5 |  | Age | 41136 | 11.5
| Condition | Good |  | 0.75 |  | Condition | Good | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Pumps | Location |  |  |  | Inter. Data Facility (IDF #1) | Location | un34
| Description |  |  |  |  | Description | wall mounted
| Age |  |  |  |  | Age | 41100 | 8.5
| Condition |  |  |  |  | Condition | Good | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Storage Tanks | Location |  |  |  | IDF #1, HVAC Terminal Units | Location
| Description |  |  |  |  | Description | Other (describe)
| Age |  |  |  |  | Age | 30+ | 30
| Condition |  |  |  |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | exhaust vent
Fuel Fired Boilers | Location | 2nd floor un; un13 |  |  | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | electric boiler in 2nd floor un |  |  |  | Notes
Furnaces | Location |  |  |  | Inter. Data Facility (IDF #2) | Location | 318
| Description |  |  |  |  | Description | wall mounted
| Age |  |  |  |  | Age | 41100 | 8.5
| Condition |  |  |  |  | Condition | Good | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Unit Ventilators | Location |  |  |  | IDF #2, HVAC Terminal Units | Location
| Description |  |  |  |  | Description | Other (describe)
| Age |  |  |  |  | Age | 30+ | 30
| Condition |  |  |  |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | exhaust vent
Fan Coil Units | Location |  |  |  | IDF #2, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Water Chillers | Location | 2nd floor un |  |  | Inter. Data Facility (IDF #3) | Location
| Description | Electric Powered |  |  |  | Description
| Age | 0 | 10 | 5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 1 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Cooling Towers | Location |  |  |  | IDF #3, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Packaged Terminal Air Conditioner | Location |  |  |  | IDF #3, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Hydronic Piping System | Location |  |  |  | Inter. Data Facility (IDF #4) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Pumps | Location | 2nd floor un; un13 |  |  | IDF #4, HVAC Terminal Units | Location
| Description | Steam Condensate Pumps |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | new pumps in 2nd floor un |  |  |  | Notes
Steam Piping System | Location | un13 |  |  | IDF #4, Packaged Terminal Air Conditioner | Location
| Description | Two Pipe |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Air Distribution | Location | typical |  |  | Inter. Data Facility (IDF #5) | Location
| Description | Sheet Metal Ducts |  |  |  | Description
| Age | 0 | 15 | 7.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Air Handling Units | Location | 2nd floor un |  |  | IDF #5, HVAC Terminal Units | Location
| Description | Indoor Air Handling Units (AHU) |  |  |  | Description
| Age | 41233 |  | 10.5 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 5 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | including 2 rooftop units |  |  |  | Notes
HVAC Fans | Location | 2nd floor un |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  |  | Description
| Age | 41233 |  | 10.5 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | centrifugal exhaust fan |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location |  |  |  | Backbone Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fire/Suppression (Standpipes), Water/Based | Location |  |  |  | Horizontal Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | sub/basement
| Description | Diesel Engine Generators
| Age | 0 | 15 | 7.5
| Condition | Good |  | 0.75
CheckBox
Quantity
| Voltage | 208 volts
Power Output
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | 2nd floor un
| Description | D5010 120
| Age | 31 | 45 | 38
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Voice Communication Terminal Equipment | Location | sub/basement
| Description | PDX/Key Systems
| Age | 0 | 10 | 5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | un86
| Description | Public Address and Mass Notification Systems
| Age | 0 | 10 | 5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Video Surveillance Systems | Location | ent/1
| Description | Analog Video Recording Devices
| Age | 41233 |  | 10.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | un86
| Description | Fire Alarm Annunciation Panels
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
| Description | 1 incinerator not in use; compressed air
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Exterior | Question | Value1 |  | Average1
Exterior | Seg ID | 1266 |  |  | SiteElements | Seg ID | 298
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 0 |  |  |  | Addition | 0
| Year Built | 1976 |  |  |  | Year Built | 1976
(Foundation) Walls for Subgrade Enclosures, Primary | Location | Typ. |  |  | Roadways | Location | S/5
| Description | Brick w/ CMU B/U |  |  |  | Description | Asphalt (Bituminous)
| Age | 31 | 45 | 38 |  | Age | 30+ |  | 30
| Condition | Good |  | 0.75 |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location |  |  |  | Parking Lots | Location | S/5
| Description |  |  |  |  | Description | Asphalt (Bituminous)
| Age |  |  |  |  | Age | 30+ |  | 30
| Condition |  |  |  |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Standard Slabs On Grade, Primary | Location | UN12 |  |  | Pedestrian Plazas and Walkways, Primary | Location | S/2
| Description | Concrete, Cast/In/Place |  |  |  | Description | Concrete, CIP
| Age | 31 | 45 | 38 |  | Age | 30+ |  | 30
| Condition | Good |  | 0.75 |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Standard Slabs On Grade, Secondary | Location |  |  |  | Pedestrian Plazas and Walkways, Secondary | Location | S/1, S/2
| Description |  |  |  |  | Description | Asphalt (Bituminous)
| Age |  |  |  |  | Age | 30+ |  | 30
| Condition |  |  |  |  | Condition | Poor |  | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Floor Construction, Primary | Location | Typ. |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location
| Description | Steel Framing, w/ Steel Deck |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Floor Construction, Secondary | Location |  |  |  | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Roof Construction, Structural Frame, Primary | Location | Typ. |  |  | Site Lighting, Primary | Location | Typ.
| Description | Steel Framing, w/ Steel Deck |  |  |  | Description | Pole Mounted H.I.D.
| Age | 31 | 45 | 38 |  | Age | 41136 |  | 11.5
| Condition | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Roof Construction, Structural Frame, Secondary | Location |  |  |  | Site Lighting, Secondary | Location | Typ.
| Description |  |  |  |  | Description | Building Mounted H.I.D.
| Age |  |  |  |  | Age | 30+ |  | 30
| Condition |  |  |  |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Walls / Exterior Assembly, Primary | Location | Typ. |  |  | Playground Surface | Location | S/6
| Description | Other (describe) |  |  |  | Description | Asphalt (Bituminous)
| Age | 31 | 45 | 38 |  | Age | 16 | 21 | 18.5
| Condition | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Brick w/ CMU back up, |  |  |  | Notes
Exterior Walls / Exterior Assembly, Secondary | Location | Typ. |  |  | Playground Equipment | Location | S/6
| Description | Other (describe) |  |  |  | Description | Multi/Component Play Equipment Set
| Age | 31 | 45 | 38 |  | Age | 41136 |  | 11.5
| Condition | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Per fabricated exposed aggregate panel (precast) |  |  |  | Notes | Rubberized surface
Exterior Windows, Primary | Location | Typ. |  |  | TCUs | Location
| Description | Aluminum, Double Hung |  |  |  | Description
| Age | 41136 |  | 11.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Screens, Insect / Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary | Location | Stair wells
| Description | Aluminum, Awning/Hopper
| Age | 41136 |  | 11.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
| Description | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location | Typ.
| Description | Fiber Reinforced Panel (FRP)
| Age | 0 | 15 | 7.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location | Roof
| Description | Polyurethane, Spray Applied
| Age | 41136 |  | 11.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Drain clogged
Roofing, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location | Roof
| Description | Aluminum
| Age | 41136 |  | 11.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location | Roof
| Description | Other (describe)
| Age | 30+ |  | 30
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Internal roof drain cast iron
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes