## FCI Summary
Building Name: | Ivy Hill | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 78694
Number of Floors: | 4
School Age (years): | 81
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 24.63%
Facility Condition = | FAIR
FCI Deficiency Cost = | 3996992.6559
FCI Replacement Cost = | 16230637.5
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 552
Historic 2005 LRFP Capacity = | 604.829
Adjusted 2012 Capacity = | 544
Recent Occupancy % = | 101.5%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 86.9%
Classroom Adequacy = | GOOD
Special Spaces Adequacy % Score = | 73.74%
Special Spaces Adequacy = | POOR

## Uniformat FCI
Building Name: |  | Ivy Hill | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 78694
Largest Floor Level Area: |  | 35423
Vertical FAR Ratio: |  | 2.2216
School Age (years): |  | 81
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 2.7% | 5.5687 | 78694 | 438227.2125 | 100 | 81 | 19 | 0.5 | 50 | 69 | 302376.7766 | 135850.4359 | 31%
|  |  | A1030 - SLAB ON GRADE | 2.65% | 5.4656 | 78694 | 430111.8937 | 100 | 81 | 19 | 0.5 | 50 | 69 | 296777.2067 | 133334.6871 | 31%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 78694 | 357074.025 | 100 | 81 | 19 | 0.5 | 50 | 69 | 246381.0772 | 110692.9478 | 31%
|  |  | SUBTOTAL SUBSTRUCTURE | 7.55% | 15.5719 | 78694 | 1225413.1313
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 78694 | 1785370.125 | 100 | 81 | 19 | 0.5 | 50 | 69 | 1231905.3862 | 553464.7388 | 31%
|  |  | B1020 - ROOF CONSTRUCTION | 3.4% | 7.0125 | 78694 | 551841.675 | 100 | 81 | 19 | 0.5 | 50 | 69 | 380770.7558 | 171070.9193 | 31%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 7.7% | 15.8812 | 78694 | 1249759.0875 | 100 | 81 | 19 | 0.53611 | 53.6111 | 72.6111 | 907463.9596 | 342295.1279 | 27.39%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 4.4% | 9.075 | 78694 | 714148.05 | 30 | 9.5 | 20.5 | 0.75 | 22.5 | 30 | 714148.05 | 0 | 0%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 3% | 6.1875 | 78694 | 486919.125 | 30 | 30 | 0 | 0.4375 | 13.125 | 13.125 | 213027.1172 | 273892.0078 | 56.25%
|  |  | SUBTOTAL SHELL | 29.5% | 60.8438 | 78694 | 4788038.0625
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 78694 | 649225.5 | 60 | 55.1875 | 4.8125 | 0.55729 | 33.4375 | 38.25 | 413881.2562 | 235344.2438 | 36.25%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 78694 | 243459.5625 | 20 | 22.1915 | 0 | 0.44681 | 5 | 5 | 60864.8906 | 182594.6719 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 78694 | 649225.5 | 20 | 7.5 | 12.5 | 0.66667 | 13.3333 | 20 | 649225.5 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 78694 | 243459.5625 | 30 | 81 | 0 | 0.5 | 5 | 5 | 40576.5938 | 202882.9688 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 3.2% | 6.6 | 78694 | 519380.4 | 10 | 9.8673 | 0.13265 | 0.4949 | 4.949 | 5.0816 | 263930.04 | 255450.36 | 49.18%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 78694 | 973838.25 | 20 | 16.2653 | 3.7347 | 0.53061 | 10.6122 | 14.3469 | 698579.8875 | 275258.3625 | 28.27%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 78694 | 973838.25 | 30 | 29.1957 | 0.80435 | 0.5 | 15 | 15.8043 | 513029.281 | 460808.969 | 47.32%
|  |  | SUBTOTAL INTERIORS | 26.2% | 54.0375 | 78694 | 4252427.025
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 0.75% | 1.5469 | 78694 | 121729.7812 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 121729.7812 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 78694 | 243459.5625 | 60 | 24.8575 | 35.1425 | 0.52616 | 31.5696 | 60 | 243459.5625 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 78694 | 210998.2875 | 60 | 11.5 | 48.5 | 0.5 | 30 | 60 | 210998.2875 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 78694 | 194767.65 | 60 | 0 | 60 | 0 | 0 | 60 | 194767.65 | 0 | 0%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 78694 | 81153.1875 | 30 | 23 | 7 | 0.5 | 15 | 22 | 59512.3375 | 21640.85 | 26.67%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 2.7% | 5.5687 | 78694 | 438227.2125 | 60 | 0 | 60 | 0 | 0 | 60 | 438227.2125 | 0 | 0%
|  |  | D3020 - BOILERS | 2% | 4.125 | 78694 | 324612.75 | 60 | 23 | 37 | 0.5 | 30 | 60 | 324612.75 | 0 | 0%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4% | 8.25 | 78694 | 649225.5 | 40 | 31.5 | 8.5 | 0.375 | 15 | 23.5 | 381419.9813 | 267805.5187 | 41.25%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4% | 8.25 | 78694 | 649225.5 | 40 | 19.2732 | 20.7268 | 0.56524 | 22.6098 | 40 | 649225.5 | 0 | 0%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 2% | 4.125 | 78694 | 324612.75 | 40 | 0 | 40 | 0 | 0 | 40 | 324612.75 | 0 | 0%
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.5% | 3.0938 | 78694 | 243459.5625 | 20 | 0 | 20 | 0 | 0 | 20 | 243459.5625 | 0 | 100%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 78694 | 162306.375 | 20 | 0 | 20 | 0 | 0 | 20 | 162306.375 | 0 | 0%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 78694 | 32461.275 | 20 | 11.5 | 8.5 | 0.75 | 15 | 20 | 32461.275 | 0 | 0%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 78694 | 210998.2875 | 60 | 60 | 0 | 0.5 | 30 | 30 | 105499.1438 | 105499.1438 | 50%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 78694 | 1136144.625 | 30 | 11.8036 | 18.1964 | 0.72321 | 21.6964 | 30 | 1136144.625 | 0 | 0%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 78694 | 486919.125 | 20 | 9.5278 | 10.4722 | 0.6713 | 13.4259 | 20 | 486919.125 | 0 | 0%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 78694 | 48691.9125 | 20 | 18.3095 | 1.6905 | 0.61098 | 12.2195 | 13.91 | 33865.1969 | 14826.7156 | 30.45%
|  |  | SUBTOTAL SERVICES | 34.25% | 70.6406 | 78694 | 5558993.3438
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 78694
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 78694
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 78694
|  |  | E1090 - OTHER EQUIPMENT |  |  | 78694
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 78694
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 78694
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 78694
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 78694
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 78694
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 78694 | 162306.375 | 30 | 11.5 | 18.5 | 0.5 | 15 | 30 | 162306.375 | 0 | 0%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 78694 | 81153.1875 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 20288.2969 | 60864.8906 | 75%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 78694 | 81153.1875 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 20288.2969 | 60864.8906 | 75%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 78694 | 81153.1875 | 30 | 11.5 | 18.5 | 0.25 | 7.5 | 26 | 70332.7625 | 10820.425 | 13.33%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 78694 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 78694
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 78694 | 16230637.5 | [7 empty] | 3996992.6559 | 24.63%
100%

## Master File (Interior)
Ivy Hill
School Code: | 718
NPS Code: | 109
Street: | 107 Ivy St.
City/Town: | Newark,
Database ID: | 70
Total size (gsf):
ROOM INFORMATION | [12 empty] | 56.2444 | Ave Condition | 0.57222 | [6 empty] | 16.2653 | Ave Condition | 0.53061 | [6 empty] | 9.8673 | Ave Condition | 0.4949 | [5 empty] | 29.1957 | Ave Condition | 0.5 | [6 empty] | 22.1915 | Ave Condition | 0.44681 | [6 empty] | 55.1875 | Ave Condition | 0.55729 | [6 empty] | 29.6875 | Ave Condition | 0.54688 | [5 empty] | 20.75 | Ave Condition | 0.5625 | [5 empty] | 24.45 | Ave Condition | 0.55 | [5 empty] | 30 | Ave Condition | 0.57143 | [6 empty] | 19.4 | Ave Condition | 0.4 | [6 empty] | 7.5 | Ave Condition | 0.66667 | [6 empty] | 12.1071 | Ave Condition | 0.69643 | [5 empty] | 29.119 | Ave Condition | 0.47195 | [5 empty] | 28.6463 | Ave Condition | 0.38049 | [6 empty] | 9.9 | Ave Condition | 0.75 | [5 empty] | 11.5 | Ave Condition | 0.75 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 9.75 | Ave Condition | 0.54167 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [7 empty] | Plumbing Fixtures - Urinals | [7 empty] | Plumbing Fixtures - Showers | [7 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [7 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [7 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
8714 | UN-1 | Gym | Ground Floor | B | Phys. Ed. (Gym + Storage) |  |  | 4118 | 19' 7" | CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  | structural facing tile wainscot | Sheet Vinyl | 20+ |  | 20 | Fair | 0.5 |  |  | continuos crack | Painted Walls with Wainscot | 10+ |  | 10 | Good | 0.75 |  |  | structural facing tile wainscot | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 |  |  | structural facing tile finish | [6 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [28 empty] | HID Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  | cracked covering | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | ducted air diffusers | [24 empty] | Present | [42 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present
8715 | UN-2 | N/A | Ground Floor | A | N/A |  |  | 120 | N/A
8716 | UN-3 | N/A | Ground Floor | A | N/A |  |  | 254 | N/A
8717 | UN-4 | N/A | Ground Floor | A | N/A |  |  | 181 | N/A
8718 | UN-5 | Locker Room | Ground Floor | B | Phys. Ed. (Gym + Storage) |  |  | 1952 | 12' 6" | CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  | structural facing tile finish | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Unfinished Walls | 10+ |  | 10 | Fair | 0.5 |  |  | structural facing tile | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 |  |  | structural facing tile | [6 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [28 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  | missing coverings | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Poor | 0.25 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [42 empty] | 0 | [8 empty] | 0 | [8 empty] | 0
8719 | UN-6 | Water Closet | Ground Floor | B | Phys. Ed. (Gym + Storage) |  |  | 173 | 12' 6" | CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  | structural facing tile finish | Ceramic Tile | 20+ |  | 20 | Good | 0.75 |  |  |  | Other (describe) | 10+ |  | 10 | Fair | 0.5 |  |  | structural facing tile | Plaster | 30+ | 30 | Poor | 0.25 |  |  | water damage | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 |  |  | structural facing tile | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 2 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 3 |  |  | Floor Trough | 30+ | 30 | Fair | 0.5 | 4 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [42 empty] | 0 | [8 empty] | 0 | [8 empty] | 0
8720 | UN-7 | Storage | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 27 | 12' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8721 | UN-8 | N/A | Ground Floor | A | N/A |  |  | 148 | N/A
8722 | UN-9 | Classroom | Ground Floor | A | General Classroom |  |  | 423 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8723 | UN-10 | Office | Ground Floor | A | Administration |  |  | 175 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8724 | UN-11 | Library | Ground Floor | A | Media Center |  |  | 1784 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Acoustical Panel | 41136 | 11.5 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 | [9 empty] | 0 | [44 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 41136 | 11.5 | Good | 0.75 |  |  |  | Other (describe) | 41136 | 11.5 | Good | 0.75 |  |  | ducted air diffusers | [24 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 41100 |  | 8.5 | Good | 0.75 | [18 empty] | 0 | [8 empty] | 0 | [8 empty] | 1 | [72 empty] | Present - Present
8725 | UN-12 | Child Study Team | Ground Floor | A | Small Group Instruction |  |  | 375 | 9' 7" | Drywall(Gypsum)/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Good | 0.75 | [9 empty] | 0 | [44 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 41136 | 11.5 | Good | 0.75 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 41100 |  | 8.5 | Good | 0.75 | [18 empty] | 0 | [8 empty] | 0 | [8 empty] | 4 | [72 empty] | Present - Present - Present
8726 | UN-13 | Vestibule | Ground Floor | A | Support |  |  | 85 | N/A
8727 | UN-14 | Boys\' Water Closet | Ground Floor | A | Support |  |  | 283 | 9' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Sheet Vinyl | 41070 |  | 8 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 |  |  | ceramic tile wainscot | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 6 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 3 |  |  | Floor Trough | 30+ | 30 | Fair | 0.5 | 5 | [28 empty] | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  | ceiling exhaust | [24 empty] | Present - Present - Present - Present
8728 | UN-15 | Storage | Ground Floor | A | Support |  |  | 2505 | N/A
8729 | UN-16 | Storage | Ground Floor | A | Support |  |  | 568 | N/A | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Good | 0.75 | [9 empty] | 0 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 41100 |  | 8.5 | Good | 0.75 | [18 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present - Present
8730 | UN-17 | Storage | Ground Floor | A | Support |  |  | 311 | N/A
8731 | UN-18 | N/A | Ground Floor | A | N/A |  |  | 318 | N/A
8732 | UN-19 | Storage | Ground Floor | A | Support |  |  | 4605 | N/A | [9 empty] | Other (describe) | 16 | 20 | 18 | Poor | 0.25 |  |  | painted concrete | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Other (describe) | 30+ | 30 | Poor | 0.25 |  |  | painted wood | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 | [35 empty] | Present - Present - Present - Present - Present - Present | [42 empty] | 0 | [8 empty] | 0 | [8 empty] | 0
8733 | UN-20 | Kitchen | Ground Floor | A | Food Service/Assembly (K-8) |  |  | 855 | N/A | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | ceramic | Suspended Acoustical | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 |  |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | 4 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | [12 empty] | Dry Chemical | 41136 | 11.5 | Good | 0.75 |  |  | ansul | [7 empty] | Present - Present - Present - Present - Present - Present - Present | [42 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present - Present - Present
8734 | UN-21 | Cafeteria A | Ground Floor | A | Food Service/Assembly (K-8) |  |  | 1626 | 9' 8" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | ceramic tile wainscot | Acoustical Panel | 30+ | 30 | Fair | 0.5 |  |  | glued on | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 | [9 empty] | 0 | [44 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [133 empty] | Present - Present - Present - Present - Present - Present | [35 empty] | Present
8735 | UN-22 | Servery | Ground Floor | A | Food Service/Assembly (K-8) |  |  | 282 | 9' 8" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Other (describe) | 41070 |  | 8 | Poor | 0.25 |  |  | painted concrete | Painted Walls | 41067 |  | 6.5 | Fair | 0.5 |  |  |  | Acoustical Panel | 30+ | 30 | Fair | 0.5 |  |  | glued on | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [44 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 41100 |  | 8.5 | Good | 0.75 | [136 empty] | Present | [8 empty] | Present - Present
8736 | UN-23 | Cafeteria B | Ground Floor | A | Food Service/Assembly (K-8) |  |  | 1512 | 9' 8" | CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | ceramic tile wainscot | Acoustical Panel | 30+ | 30 | Fair | 0.5 |  |  | glued on | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 | [9 empty] | 0 | [44 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [169 empty] | Present - Present - Present
8737 | UN-24 | Teachers\' Room | Ground Floor | A | Faculty Support |  |  | 462 | 9' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 | [9 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [28 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Very Poor | 0.1 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 41100 |  | 8.5 | Good | 0.75 |  |  | cpu | [106 empty] | Present - Present - Present - Present - Present - Present - Present
8738 | UN-25 | Custodial Office | Ground Floor | A | Support |  |  | 273 | 9' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8739 | UN-26 | N/A | Ground Floor | A | N/A |  |  | 45 | N/A
8740 | UN-27 | N/A | Ground Floor | A | N/A |  |  | 40 | N/A
8741 | UN-28 | N/A | Ground Floor | A | N/A |  |  | 981 | N/A
8742 | UN-29 | N/A | Ground Floor | A | N/A |  |  | 228 | N/A
8743 | UN-30 | Womens' Water Closet | Ground Floor | A | Support |  |  | 351 | 9' 10" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 9 | [7 empty] | 7 | [7 empty] | 0
8744 | UN-31 | Storage | Ground Floor | A | Support |  |  | 484 | N/A
8745 | UN-32 | Custodial Closet | Ground Floor | A | Support |  |  | 31 | 9' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8746 | UN-33 | N/A | Ground Floor | A | N/A |  |  | 1083 | N/A
8747 | 101 | Literacy Coach Classroom | 1st Floor | A | Small Group Instruction |  |  | 1091 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Acoustical Panel | 30+ | 30 | Poor | 0.25 | 0 |  | Concealed spline, damage at pipes | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Ventilators | 41136 | 11.5 | Fair | 0.5 | 0 | [26 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 1 |  | Desktops | [70 empty] | Present
8748 | 102 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 679 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 |  | Desktops | [70 empty] | Present - Present
8749 | 103 | 1st GradeClassroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 743 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8750 | 104 | Health Office | 1st Floor | A | Health Services |  |  | 695 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 16 | 20 | 18 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 | [16 empty] | 0 | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 pc | [105 empty] | 0 | Present - Present - Present
8751 | 105 | Self Contained Special Education Classroom | 1st Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 771 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Wood folding partition 50, poor | [51 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [18 empty] | 1 |  | Mobile | [15 empty] | 3 |  | Desktops | [70 empty] | Present - Present - Present - Present
8752 | 106 | 1st Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 812 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 2 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present
8753 | 107 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 576 | 11' 10" | [9 empty] | Wood | [17 empty] | Plaster
8754 | 108 | Music Room | 1st Floor | A | Visual & Performing Arts |  |  | 904 | 11' 10" | Drywall(Gypsum)/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 10+ |  | 10 | Fair | 0.5 | 0 |  | Acoustical panel | Acoustical Panel | 30+ | 30 | Fair | 0.5 | 0 |  | Concealed spline | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | [26 empty] | 0 | Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 pcs | [105 empty] | 0 | Present - Present - Present - Present - Present - Present
8755 | 109 | 1st Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 614 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8756 | UN-5 | Custodial Closet | 1st Floor | A | Support |  |  | 75 | 11' 10"
8757 | UN-34 | Gym | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 3534 | 25' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Other (describe) | 41070 |  | 8 | Good | 0.75 |  |  | Rubber sports floor | Painted Walls with Wainscot | 10+ |  | 10 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [54 empty] | HID Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [133 empty] | Present - Present - Present - Present - Present - Present - Present
8758 | UN-35 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 229 | N/A
8759 | UN-36 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 248 | N/A
8760 | UN-37 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 118 | N/A
8761 | UN-38 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 233 | N/A
8762 | UN-39 | Custodial Closet | 1st Floor | A | Support |  |  | 9 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8763 | UN-40 | Boys' Water Closet | 1st Floor | A | Support |  |  | 276 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 2 | [7 empty] | 7 | [7 empty] | 10
8764 | UN-41 | Storage | 1st Floor | A | Support |  |  | 26 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8765 | UN-42 | Storage | 1st Floor | A | Support |  |  | 264 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8766 | UN-43 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 51 | 11' 10" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
8767 | UN-44 | Auditorium | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 4047 | 25' 0" | [8 empty] | N/a | Other (describe) | 20+ |  | 20 | Fair | 0.5 |  |  | Painted concrete | Other (describe) | 10+ |  | 10 | Fair | 0.5 |  |  | Painted Acoustical panels, 60 | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  | Custom pendant ceiling lights, 60 in fair | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  | Recesed ceiling and wall radiator | [24 empty] | Present - Present - Present - Present - Present - Present - Present | [133 empty] | Present - Present - Present - Present - Present - Present - Present | Auditorium speaker system
8768 | UN-45 | Storage | 1st Floor | A | Support |  |  | 146 | 8' 0" | [9 empty] | Unfinished | [17 empty] | Plaster
8769 | UN-46 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 36 | 11' 10" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
8770 | UN-47 | Main Office | 1st Floor | A | Administration |  |  | 715 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 |  |  |  | Acoustical Panel | 30+ | 30 | Fair | 0.5 |  |  | Concealed spline | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Other (describe) | 41136 | 11.5 | Good | 0.75 |  |  | Water | [7 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 2 pcs | [106 empty] | Present - Present - Present - Present - Present - Present - Present
8771 | UN-48 | N/A | 1st Floor | A | Administration |  |  | 110 | N/A
8772 | UN-49 | N/A | 1st Floor | A | Administration |  |  | 46 | N/A
8773 | UN-50 | N/A | 1st Floor | A | Administration |  |  | 297 | N/A | Drywall(Gypsum)/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 |  |  |  | Acoustical Panel | 30+ | 30 | Fair | 0.5 |  |  | Concealed Spline | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 | [16 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 pc | [105 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
8774 | UN-51 | N/A | 1st Floor | A | Administration |  |  | 85 | N/A
8775 | UN-52 | Vice Principal's Office | 1st Floor | A | Administration |  |  | 177 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8776 | UN-53 | Storage | 1st Floor | A | Administration |  |  | 33 | 11' 10"
8777 | UN-54 | Storage | 1st Floor | A | Administration |  |  | 20 | N/A
8778 | UN-55 | Storage | 1st Floor | A | Administration |  |  | 28 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8779 | UN-56 | Storage | 1st Floor | A | Administration |  |  | 22 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8780 | UN-57 | Custodial Closet | 1st Floor | A | Support |  |  | 77 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8781 | UN-58 | Storage | 1st Floor | A | Support |  |  | 133 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8782 | UN-59 | Storage | 1st Floor | A | Support |  |  | 258 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8783 | UN-60 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 40 | 11' 10" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
8784 | UN-61 | Custodial Closet | 1st Floor | A | Support |  |  | 9 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8785 | UN-62 | Girls\' Water Closet | 1st Floor | A | Support |  |  | 283 | 12' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Epoxy | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 41004 |  | 4.5 | Fair | 0.5 |  |  | Ceramic tile | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 3 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 11 | [7 empty] | 0 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present
8786 | UN-63 | Storage | 1st Floor | A | Support |  |  | 24 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8787 | UN-64 | Small Group Instruction | 1st Floor | A | Small Group Instruction |  |  | 302 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Acoustical Panel | 30+ | 30 | Poor | 0.25 | 0 |  | Concealed spline, water damage on pipes | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Terminal Unit Heaters | 41136 | 11.5 | Fair | 0.5 | 0 | [26 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present - Present - Present
8788 | UN-65 | Water Closet | 1st Floor | A | Small Group Instruction |  |  | 72 | 11' 10" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
8789 | UN-66 | N/A | 1st Floor | A | N/A |  |  | 284 | N/A
8790 | UN-67 | N/A | 1st Floor | A | N/A |  |  | 62 | N/A
8791 | UN-68 | N/A | 1st Floor | A | N/A |  |  | 61 | N/A
8792 | UN-69 | Lockers | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 566 | N/A
8793 | UN-70 | Showers | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 322 | N/A
8794 | UN-71 | Water Closet | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 190 | N/A
8795 | 200 | 4th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 739 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8796 | 201 | 4th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 739 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8797 | 202 | 3rd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 730 | 11' 11" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Very Good | 0.9 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 |  | Desktops | [70 empty] | Present
8798 | 203 | 4th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 746 | 11' 10" | [9 empty] | Wood | [17 empty] | Plaster
8799 | 204 | Classroom | 2nd Floor | A | General Classroom |  |  | 712 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8800 | 205 | Technology Coordinator Classroom | 2nd Floor | A | Technological Literacy |  |  | 793 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8801 | 206 | 3rd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 781 | 11' 10" | [9 empty] | Wood | [17 empty] | Plaster
8802 | 207 | 7th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 715 | 11' 10" | [9 empty] | Wood | [17 empty] | Acoustical Panel
8803 | 208 | 3rd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 782 | 11' 10" | [9 empty] | Wood | [17 empty] | Plaster
8804 | 209 | Literacy Tutor Classroom | 2nd Floor | A | Small Group Instruction |  |  | 740 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 |  |  | 2 | [15 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 11 |  | Desktops | [70 empty] | Present - Present
8805 | 210 | Vice Principal's Office | 2nd Floor | A | Administration |  |  | 407 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8806 | 211 | Art Classroom | 2nd Floor | A | Visual & Performing Arts |  |  | 1111 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  | Hole in pipe of ceiling | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | [26 empty] | 0 | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 4. Pcs | [105 empty] | 0 | Present - Present - Present
8807 | 212 | 2nd Grade Classroom | 2nd Floor | B | General Classroom (Grades 1-3) |  |  | 795 | 11' 11" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 46 | 60 | 53 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 |  | Desktops | [70 empty] | Present - Present - Present - Present
8808 | 213 | Self-Contained Special Education Classroom | 2nd Floor | B | Self-Contained Sp. Ed. Classroom |  |  | 801 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 46 | 60 | 53 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present
8809 | 214 | 2nd Grade Inclusion Classroom | 2nd Floor | B | Self-Contained Sp. Ed. Classroom |  |  | 769 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 46 | 60 | 53 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 1 |  | Desktop | [70 empty] | Present - Present - Present - Present - Present - Present
8810 | 215 | 2nd Grade Bilingual Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 822 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8811 | UN-72 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 294 | 12' 0" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 4 | [7 empty] | 3 | [7 empty] | 4
8812 | UN-73 | Custodial Closet | 2nd Floor | A | Support |  |  | 15 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8813 | UN-74 | Storage | 2nd Floor | A | Support |  |  | 14 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8814 | UN-75 | Storage | 2nd Floor | A | Support |  |  | 13 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8815 | UN-76 | Storage | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 9 | 11' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8816 | UN-77 | Storage | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 7 | 11' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8817 | UN-78 | Faculty Lounge | 2nd Floor | A | Faculty Support |  |  | 457 | 12' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | [5 empty] | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 |  |  | Cast iron | [24 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present - Present - Present - Present
8818 | UN-79 | Custodial Closet | 2nd Floor | A | Support |  |  | 9 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8819 | UN-80 | Storage | 2nd Floor | A | Support |  |  | 26 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8820 | UN-81 | Boys\' Water Closet | 2nd Floor | A | Support |  |  | 277 | 12' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Epoxy | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 41004 |  | 4.5 | Fair | 0.5 |  |  | Ceramic tile | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 2 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Poor | 0.25 | 7 |  |  | Floor Unit | 30+ | 30 | Poor | 0.25 | 10 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Fair | 0.5 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Very Poor | 0.1 | [27 empty] | Present
8821 | UN-82 | Guidance Office | 2nd Floor | A | Administration |  |  | 264 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8822 | UN-83 | Storage | 2nd Floor | A | Support |  |  | 163 | N/A
8823 | UN-84 | Womens' Water Closet | 2nd Floor | A | Faculty Support |  |  | 34 | 12' 0" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
8824 | UN-85 | N/A | 2nd Floor | A | N/A |  |  | 50 | N/A
8825 | UN-86 | N/A | 2nd Floor | A | N/A |  |  | 50 | N/A
8826 | UN-87 | Teachers\' Room | 2nd Floor | A | Faculty Support |  |  | 417 | 11' 10" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 |  |  |  | Suspended Acoustical | 41136 | 11.5 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 |  |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 | [16 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 pc | [105 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
8827 | UN-88 | Mens' Water Closet | 2nd Floor | A | Faculty Support |  |  | 31 | 12' 0" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
8828 | UN-89 | Storage | 2nd Floor | A | Support |  |  | 147 | N/A
8829 | UN-90 | Office | 2nd Floor | A | Administration |  |  | 256 | 11' 10" | [8 empty] | N/a | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Good | 0.75 | [54 empty] | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 1 pc | [106 empty] | Present - Present - Present - Present - Present - Present - Present
8830 | UN-91 | Custodial Closet | 2nd Floor | A | Support |  |  | 9 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8831 | UN-92 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 283 | 12' 0" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 3 | [7 empty] | 11 | [7 empty] | 0
8832 | UN-93 | Storage | 2nd Floor | A | Support |  |  | 25 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8833 | UN-94 | Storage | 2nd Floor | A | Support |  |  | 234 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8834 | UN-95 | Book Storage | 2nd Floor | A | Support |  |  | 374 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8835 | UN-96 | Storage | 2nd Floor | A | Support |  |  | 228 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8836 | 301 | ESL Classroom | 3rd Floor | A | General Classroom |  |  | 740 | 12' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Poor | 0.25 | 0 |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 |  | Desktops | [70 empty] | Present
8837 | 302 | Classroom | 3rd Floor | A | General Classroom |  |  | 745 | 12' 0" | [9 empty] | Wood | [17 empty] | Plaster
8838 | 303 | Classroom | 3rd Floor | A | General Classroom |  |  | 730 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8839 | 304 | Classroom | 3rd Floor | A | General Classroom |  |  | 745 | 11' 8" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  | Peeling | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 |  | Desktop | [70 empty] | Present - Present
8840 | 305 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 712 | 12' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 16 | 20 | 18 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 5 |  | Desktops | [70 empty] | Present - Present - Present
8841 | 306 | 8th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 793 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8842 | 307 | Teachers' Room | 3rd Floor | A | Faculty Support |  |  | 416 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8843 | 308 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 781 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8844 | 309 | 6th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 715 | 12' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [18 empty] | 1 |  | Wall mount | [15 empty] | 5 |  | Desktops | [70 empty] | Present - Present - Present - Present
8845 | 311 | Computer Lab | 3rd Floor | A | Technological Literacy |  |  | 1346 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8846 | 312 | 6th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 778 | 12' 0" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 | 0 |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Poor | 0.25 | 0 | [26 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 4 | [33 empty] | 5 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present
8847 | 313 | 6th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 745 | 12' 0" | [9 empty] | Wood | [17 empty] | Plaster
8848 | 314 | Classroom | 3rd Floor | A | General Classroom |  |  | 795 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8849 | 315 | 5th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 797 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8850 | 316 | 5th Grade Classroom | 3rd Floor | B | General Classroom (Grades 4-5) |  |  | 769 | 12' 4" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 46 | 60 | 53 | Fair | 0.5 | [54 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Fin Tube | 30+ | 30 | Poor | 0.25 | [27 empty] | Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [18 empty] | 1 |  | Wall mount | [15 empty] | 3 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present - Present
8851 | 317 | 5th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 769 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8852 | 318 | Classroom | 3rd Floor | A | General Classroom |  |  | 759 | 11' 6" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8853 | 319 | Science Lab | 3rd Floor | A | Science (6-12) |  |  | 820 | 11' 6" | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [53 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Radiators | 30+ | 30 | Fair | 0.5 | 0 | [26 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [18 empty] | 1 |  | Wall mount | [15 empty] | 1 |  | Desktop | [7 empty] | Present | [17 empty] | Present | [17 empty] | Present | 8 | [25 empty] | Present - Present - Present - Present - Present - Present - Present
8854 | UN-97 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 298 | 12' 0" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 4 | [7 empty] | 5 | [7 empty] | 0
8855 | UN-98 | Custodial Closet | 3rd Floor | A | Support |  |  | 15 | 12' 0" | [9 empty] | Unfinished | [17 empty] | Plaster
8856 | UN-99 | Storage | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 14 | 12' 0 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8857 | UN-100 | Storage | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 12 | 12' 0 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8858 | UN-101 | Storage | 3rd Floor | A | General Classroom |  |  | 9 | 12' 0 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8859 | UN-102 | Storage | 3rd Floor | A | General Classroom |  |  | 7 | 12' 0 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8860 | UN-103 | Storage | 3rd Floor | A | Support |  |  | 7 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8861 | UN-104 | Storage | 3rd Floor | A | Support |  |  | 6 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8862 | UN-105 | Storage | 3rd Floor | A | Support |  |  | 10 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8863 | UN-106 | Storage | 3rd Floor | A | Support |  |  | 10 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8864 | UN-107 | Custodial Closet | 3rd Floor | A | Support |  |  | 9 | 12' 0" | [9 empty] | Unfinished | [17 empty] | Plaster
8865 | UN-108 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 269 | 12' 0" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 2 | [7 empty] | 7 | [7 empty] | 11
8866 | UN-109 | Storage | 3rd Floor | A | Support |  |  | 33 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8867 | UN-110 | N/A | 3rd Floor | A | N/A |  |  | 175 | N/A
8868 | UN-111 | Storage | 3rd Floor | A | Support |  |  | 53 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8869 | UN-112 | Storage | 3rd Floor | A | Support |  |  | 53 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8870 | UN-113 | Custodial Closet | 3rd Floor | A | Support |  |  | 9 | 12' 0" | [9 empty] | Unfinished | [17 empty] | Plaster
8871 | UN-114 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 283 | 12' 0" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 3 | [7 empty] | 11 | [7 empty] | 0
8872 | UN-115 | Storage | 3rd Floor | A | Support |  |  | 25 | 12' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12608 | UN-122 |  | Ground Floor | A
12605 | UN-119 |  | Ground Floor | A
12606 | UN-120 |  | Ground Floor | A
12603 | UN-116 |  | Ground Floor | A
12604 | UN-118 |  | Ground Floor | A
12607 | UN-121 |  | Ground Floor | A
12609 | UN-123 |  | Ground Floor | A
12610 | UN-124 |  | Ground Floor | A
12611 | UN-125 |  | Ground Floor | A
12612 | UN-126 |  | Ground Floor | A
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
51 | A | UN-44 (auditorium) | 1st | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 | [12 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on Metal Lath | [9 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | [19 empty] | Present
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [7 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
158 | A | Building phase C | 3rd | [6 empty] | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  | Cracking | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 |  |  | Concealed spline - damage at light fixtures and dents | [26 empty] | Other (describe) | 31 | 45 | 38 | Fair | 0.5 |  |  | Steel - some missing lock | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Fair | 0.5 |  |  | Missing cover | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Good | 0.75 |  |  | On ceiling | [16 empty] | Present | [16 empty] | Present
159 | B | @ 101 (classroom) | 1st | [6 empty] | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Brick veneer wainscot | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 |  |  | Concealed spline - damage at corridor corner | [8 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on metal lath | Full Recessed Stainless Steel Drinking Fountains | 0 | 7 | 3.5 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Steel | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Good | 0.75 |  |  |  | Other (describe) | 0 | 7 | 3.5 | Fair | 0.5 |  |  | Water based | [7 empty] | Present | [16 empty] | Present | [7 empty] | Present
160 | C | Building Phase B | 3rd | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  | Isolated cracks | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 |  |  | Masonry wainscot - cracks on masonry and chipped paint | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 |  |  | Glued | [8 empty] | Plaster/Metal Stud Framing | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Full Recessed Stainless Steel Drinking Fountains | 0 | 7 | 3.5 | Fair | 0.5 |  |  | Bent | Other (describe) | 46 | 60 | 53 | Fair | 0.5 |  |  | Steel | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 0 | 7 | 3.5 | Fair | 0.5 |  |  | Water based | [7 empty] | Present | [16 empty] | Present | [7 empty] | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [7 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [7 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
154 | A | @ UN-47 (main office) | All | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Steel Pan | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Brick veneer wainscot | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | Painted concrete | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Painted concrete - some nosing chipped off | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Painted concrete | Labeled Metal/Metal Frames | 41070 |  | 8 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | [35 empty] | Present | At roof access
155 | B | @ 101 (classroom) | All | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Poor | 0.25 |  |  | Water damage | Steel Pan | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 |  |  | Brick veneer wainscot | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | Painted concrete | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Painted concrete | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Painted concrete | Labeled Metal/Metal Frames | 41070 |  | 8 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | [35 empty] | Present | At roof access
156 | C | UN-72 (boys water closet) | All | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Steel Pan | 30+ |  | 30 | Good | 0.75 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Poor | 0.25 |  |  | Water damage | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Labeled Metal/Metal Frames | 41070 |  | 8 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5

## Master File (Systems)
systems | Question | Value1 |  | Average1 | systems | Question | Value1 |  | Average1
Systems | Seg ID | 1448 |  |  | InfoTech | Seg ID | 457
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 0 |  |  |  | Addition | 0
| Year Built | 1932 |  |  |  | Year Built | 1932
Domestic Water Heaters | Location | UN/28 |  |  | Entrance Facilities (Demarc or Cable Vault) | Location
| Description | Fuel/Fired Water Heater |  |  |  | Description
| Age | 41136 |  | 11.5 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Pumps for domestic hot water in fair condition |  |  |  | Notes
Sanitary Drainage | Location |  |  |  | Main Dist. Facility (MDF) | Location | Basement Level
| Description |  |  |  |  | Description | cabinet
| Age |  |  |  |  | Age | 41100 |  | 8.5
| Condition |  |  |  |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | room UN/29
Building Support (other) Plumbing Systems | Location | UN/28 |  |  | MDF, HVAC Terminal Units | Location
| Description | Stormwater Drainage Sump Pumps |  |  |  | Description
| Age | 16 | 30 | 23 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Piping | Location | UN/28 |  |  | MDF, Packaged Terminal Air Conditioner | Location
| Description | Gas Piping |  |  |  | Description
| Age | 16 | 30 | 23 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Pumps | Location |  |  |  | Inter. Data Facility (IDF #1) | Location | UN/52
| Description |  |  |  |  | Description | wall mounted rack
| Age |  |  |  |  | Age | 41100 |  | 8.5
| Condition |  |  |  |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Storage Tanks | Location |  |  |  | IDF #1, HVAC Terminal Units | Location
| Description |  |  |  |  | Description | Cast Iron Radiators
| Age |  |  |  |  | Age | 30+ |  | 30
| Condition |  |  |  |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Fired Boilers | Location | UN/28 |  |  | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers |  |  |  | Description | Window Mounted
| Age | 16 | 30 | 23 |  | Age | 0 | 7 | 3.5
| Condition | Fair |  | 0.5 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | 2 |  |  |  | Notes
Furnaces | Location |  |  |  | Inter. Data Facility (IDF #2) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Unit Ventilators | Location |  |  |  | IDF #2, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fan Coil Units | Location |  |  |  | IDF #2, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Water Chillers | Location |  |  |  | Inter. Data Facility (IDF #3) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Cooling Towers | Location |  |  |  | IDF #3, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Packaged Terminal Air Conditioner | Location |  |  |  | IDF #3, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Hydronic Piping System | Location |  |  |  | Inter. Data Facility (IDF #4) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Pumps | Location |  |  |  | IDF #4, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Steam Piping System | Location | Typical |  |  | IDF #4, Packaged Terminal Air Conditioner | Location
| Description | Two Pipe |  |  |  | Description
| Age | 16 | 30 | 23 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Air Distribution | Location |  |  |  | Inter. Data Facility (IDF #5) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Air Handling Units | Location |  |  |  | IDF #5, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Fans | Location | Roof A |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  |  | Description
| Age | 40+ |  | 40 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | rooftop exhaust fan |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location |  |  |  | Backbone Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fire/Suppression (Standpipes), Water/Based | Location |  |  |  | Horizontal Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | UN/28
| Description | Diesel Engine Generators
| Age | 0 | 15 | 7.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
| Power Output | 62.5 kva
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | UN/17
| Description | D5010 120
| Age | 60+ |  | 60
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Voice Communication Terminal Equipment | Location | UN/20
| Description | PDX/Key Systems
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | UN/87
| Description | Public Address and Mass Notification Systems
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Video Surveillance Systems | Location | ENT/1
| Description | Analog Video Recording Devices
| Age | 41233 |  | 10.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | UN/26
| Description | Fire Alarm Annunciation Panels
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | head end
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
| Description | hot water storage tank; poor; 60+
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Value2 |  | Average2 | Value3 |  | Average3 | Exterior | Question | Value1 | Average1
Exterior | Seg ID | 1767 |  |  | 1782 |  |  | 2116 |  |  | SiteElements | Seg ID | 406
| Bldg.Phase | A |  |  | B |  |  | C |  |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  | 0 |  |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  | 1 |  |  |  | Addition | 0
| Year Built | 1932 |  |  | 1957 |  |  | 1970 |  |  |  | Year Built | 1932
(Foundation) Walls for Subgrade Enclosures, Primary | Location | Tpical |  |  | Typical | [5 empty] | Roadways | Location | S/4
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place | [6 empty] | Description | Concrete
| Age | 60+ |  | 60 | 46 | 60 | 53 |  |  |  |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  |  |  |  | Condition | Fair | 0.5
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location | [9 empty] | Parking Lots | Location | S/3
| Description | [10 empty] | Description | Asphalt (Bituminous)
| Age | [10 empty] | Age | 41136 | 11.5
| Condition | [10 empty] | Condition | Fair | 0.5
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Standard Slabs On Grade, Primary | Location | Typical |  |  | Typical | [5 empty] | Pedestrian Plazas and Walkways, Primary | Location | S/2, S/6, S/8, S/10, S/12
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place | [6 empty] | Description | Concrete, CIP
| Age | 60+ |  | 60 | 46 | 60 | 53 |  |  |  |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  |  |  |  | Condition | Poor | 0.25
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Standard Slabs On Grade, Secondary | Location | [9 empty] | Pedestrian Plazas and Walkways, Secondary | Location
| Description | [10 empty] | Description
| Age | [10 empty] | Age
| Condition | [10 empty] | Condition
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Floor Construction, Primary | Location | Typical |  |  | Typical |  |  | Typical |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location
| Description | Concrete, PC Beams and Deck |  |  | Concrete, PC Beams and Deck |  |  | Steel Framing, w/ PC Planks |  |  |  | Description
| Age | 60+ |  | 60 |  |  |  | 31 | 45 | 38 |  | Age
| Condition | Fair |  | 0.5 |  |  |  | Fair |  | 0.5 |  | Condition
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Floor Construction, Secondary | Location | [9 empty] | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description | [10 empty] | Description
| Age | [10 empty] | Age
| Condition | [10 empty] | Condition
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Roof Construction, Structural Frame, Primary | Location | Typical |  |  | Typical |  |  | Typical |  |  | Site Lighting, Primary | Location | Typical
| Description | Concrete, PC Beams and Deck |  |  | Concrete, PC Beams and Deck |  |  | Steel Framing, w/ PC Planks |  |  |  | Description | Pole Mounted H.I.D.
| Age | 60+ |  | 60 |  |  |  | 31 | 45 | 38 |  | Age | 41136 | 11.5
| Condition | Fair |  | 0.5 |  |  |  | Fair |  | 0.5 |  | Condition | Good | 0.75
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Roof Construction, Structural Frame, Secondary | Location | [9 empty] | Site Lighting, Secondary | Location
| Description | [10 empty] | Description
| Age | [10 empty] | Age
| Condition | [10 empty] | Condition
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Exterior Walls / Exterior Assembly, Primary | Location | Typical |  |  | Typical |  |  | Typical |  |  | Playground Surface | Location | S/1
| Description | Other (describe) |  |  | Other (describe) |  |  | Brick Veneer w/ Steel Stud |  |  |  | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 | 46 | 60 | 53 | 31 | 45 | 38 |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 | Fair |  | 0.5 |  | Condition | Poor | 0.25
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | Brick w/ masonry backup wall |  |  | Brick veneer on masonry | [6 empty] | Notes
Exterior Walls / Exterior Assembly, Secondary | Location | Typical | [8 empty] | Playground Equipment | Location | S/1
| Description | Stone Veneer w/ CMU B/U | [9 empty] | Description | B/Ball Backstops
| Age | 60+ |  | 60 | [7 empty] | Age | 41136 | 11.5
| Condition | Fair |  | 0.5 | [7 empty] | Condition | Poor | 0.25
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | Cast/stone | [9 empty] | Notes
Exterior Windows, Primary | Location | Typical |  |  | Typical |  |  | Typical |  |  | TCUs | Location
| Description | Aluminum, Double Hung |  |  | Aluminum, Double Hung |  |  | Aluminum, Awning/Hopper |  |  |  | Description
| Age | 41136 |  | 11.5 | 41136 |  | 11.5 | 41136 |  | 11.5 |  | Age
| Condition | Good |  | 0.75 | Good |  | 0.75 | Good |  | 0.75 |  | Condition
| CheckBox | [10 empty] | CheckBox
| Quantity | [10 empty] | Quantity
| Voltage | [10 empty] | Voltage
| Power Output | [10 empty] | Power Output
| Elec Power | [10 empty] | Elec Power
| Notes | [10 empty] | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated) |  |  | Glass, Double Pane (Insulated) |  |  | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Screens, Insect / Security Grilles |  |  | Screens, Insect / Security Grilles |  |  | Screens, Insect / Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary | Location | Typical |  |  | Typical
| Description | Aluminum, Awning/Hopper |  |  | Aluminum, Awning/Hopper
| Age | 41136 |  | 11.5 | 41136 |  | 11.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
| Description | Glass, Double Pane (Insulated) |  |  | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
| CheckBox | Screens, Insect / Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location | Typical |  |  | Typical
| Description | Fiber Reinforced Panel (FRP) |  |  | Fiber Reinforced Panel (FRP)
| Age | 0 | 15 | 7.5 | 0 | 15 | 7.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location | Typical |  |  | Typical |  |  | Typical
| Description | Polyurethane, Spray Applied |  |  | Polyurethane, Spray Applied |  |  | Polyurethane, Spray Applied
| Age | 30+ |  | 30 | 30+ |  | 30 | 30+ |  | 30
| Condition | Poor |  | 0.25 | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Water damage @ center roof
Roofing, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location | Typical |  |  | Typical |  |  | Typical
| Description | Aluminum |  |  | Other (describe) |  |  | Aluminum
| Age | 30+ |  | 30 | 30+ |  | 30 | 30+ |  | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Flashing and spray applied polyurethane at parapet |  |  | Spray applied polyurethane at parapet
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location | Typical |  |  | Typical |  |  | Typical
| Description | Aluminum |  |  | Other (describe) |  |  | Aluminum
| Age | 30+ |  | 30 | 30+ |  | 30 | 30+ |  | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Gutters and downspout and Cast iron internal roof drains at center roof |  |  | Cast iron internal drain |  |  | Gutters and downspout
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes