## FCI Summary
Building Name: | Mount Vernon | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 110289
Number of Floors: | B + 2
School Age (years): | 57
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 13.77%
Facility Condition = | GOOD
FCI Deficiency Cost = | 3133294.63
FCI Replacement Cost = | 22747106.25
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 676
Historic 2005 LRFP Capacity = | 864
Adjusted 2012 Capacity = | 806
Recent Occupancy % = | 83.87%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 94.8%
Classroom Adequacy = | GOOD
Special Spaces Adequacy % Score = | 75.86%
Special Spaces Adequacy = | POOR

## Uniformat FCI
Building Name: |  | Mount Vernon | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 110289
Largest Floor Level Area: |  | 64550
Vertical FAR Ratio: |  | 1.7086
School Age (years): |  | 57
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 3.5% | 7.2188 | 110289 | 796148.7188 | 100 | 57 | 43 | 0.5 | 50 | 93 | 740418.3084 | 55730.4103 | 7%
|  |  | A1030 - SLAB ON GRADE | 3.8% | 7.8375 | 110289 | 864390.0375 | 100 | 57 | 43 | 0.625 | 62.5 | 100 | 864390.0375 | 0 | 0%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 110289 | 500436.3375 | 100 | 57 | 43 | 0.625 | 62.5 | 100 | 500436.3375 | 0 | 0%
|  |  | SUBTOTAL SUBSTRUCTURE | 9.5% | 19.5938 | 110289 | 2160975.0938
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 110289 | 2502181.6875 | 100 | 57 | 43 | 0.625 | 62.5 | 100 | 2502181.6875 | 0 | 0%
|  |  | B1020 - ROOF CONSTRUCTION | 4.4% | 9.075 | 110289 | 1000872.675 | 100 | 57 | 43 | 0.625 | 62.5 | 100 | 1000872.675 | 0 | 0%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 5.8% | 11.9625 | 110289 | 1319332.1625 | 100 | 57 | 43 | 0.50956 | 50.9559 | 93.9559 | 1239590.1744 | 79741.9881 | 6.044%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 3.3% | 6.8063 | 110289 | 750654.5063 | 30 | 19.75 | 10.25 | 0.6875 | 20.625 | 30 | 750654.5063 | 0 | 0%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 4% | 8.25 | 110289 | 909884.25 | 30 | 27.125 | 2.875 | 0.625 | 18.75 | 21.625 | 655874.8969 | 254009.3531 | 27.92%
|  |  | SUBTOTAL SHELL | 28.5% | 58.7812 | 110289 | 6482925.2812
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 110289 | 909884.25 | 60 | 48.4571 | 11.5429 | 0.57857 | 34.7143 | 46.2571 | 701477.4289 | 208406.8211 | 22.9%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 110289 | 341206.5938 | 20 | 22.5 | 0 | 0.50694 | 5 | 5 | 85301.6484 | 255904.9453 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 110289 | 909884.25 | 20 | 7.5 | 12.5 | 0.75 | 15 | 20 | 909884.25 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 110289 | 341206.5938 | 30 | 57 | 0 | 0.5 | 5 | 5 | 56867.7656 | 284338.8281 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 2.5% | 5.1562 | 110289 | 568677.6562 | 10 | 10.8056 | 0 | 0.51389 | 5 | 5 | 284338.8281 | 284338.8281 | 50%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 110289 | 1364826.375 | 20 | 17.473 | 2.527 | 0.46081 | 9.2162 | 11.7432 | 801374.4053 | 563451.9697 | 41.28%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 110289 | 1364826.375 | 30 | 17.6286 | 12.3714 | 0.58571 | 17.5714 | 29.9429 | 1362226.7057 | 2599.6693 | 0.1905%
|  |  | SUBTOTAL INTERIORS | 25.5% | 52.5938 | 110289 | 5800512.0938
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 0.5% | 1.0312 | 110289 | 113735.5312 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 113735.5312 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 110289 | 341206.5938 | 60 | 23.6741 | 36.3259 | 0.54275 | 32.5649 | 60 | 341206.5938 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 110289 | 295712.3812 | 60 | 11.5 | 48.5 | 0.25 | 15 | 60 | 295712.3812 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 110289 | 272965.275 | 60 | 60 | 0 | 0.5 | 30 | 30 | 136482.6375 | 136482.6375 | 50%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 110289 | 113735.5312 | 30 | 60 | 0 | 0.5 | 5 | 5 | 18955.9219 | 94779.6094 | 83.33%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 3.2% | 6.6 | 110289 | 727907.4 | 60 | 23 | 37 | 0.5 | 30 | 60 | 727907.4 | 0 | 0%
|  |  | D3020 - BOILERS | 2.5% | 5.1562 | 110289 | 568677.6562 | 60 | 30.25 | 29.75 | 0.5 | 30 | 59.75 | 566308.166 | 2369.4902 | 0.4167%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4.5% | 9.2812 | 110289 | 1023619.7812 | 40 | 35.375 | 4.625 | 0.4375 | 17.5 | 22.125 | 566189.6915 | 457430.0897 | 44.69%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4.5% | 9.2812 | 110289 | 1023619.7812 | 40 | 18.4552 | 21.5448 | 0.51155 | 20.4621 | 40 | 1023619.7812 | 0 | 0%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 0% | 0 | 110289 | 0 | 40 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | #DIV/0!
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.5% | 3.0938 | 110289 | 341206.5938 | 20 | 0 | 20 | 0 | 0 | 20 | 341206.5938 | 0 | 100%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 110289 | 227471.0625 | 20 | 0 | 20 | 0 | 0 | 20 | 227471.0625 | 0 | 0%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 110289 | 45494.2125 | 20 | 19.625 | 0.375 | 0.625 | 12.5 | 12.875 | 29286.8993 | 16207.3132 | 35.62%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 110289 | 295712.3812 | 60 | 53 | 7 | 0.25 | 15 | 22 | 108427.8731 | 187284.5081 | 63.33%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 110289 | 1592297.4375 | 30 | 14.1398 | 15.8602 | 0.64785 | 19.4355 | 30 | 1592297.4375 | 0 | 0%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 110289 | 682413.1875 | 20 | 6 | 14 | 0.65 | 13 | 20 | 682413.1875 | 0 | 0%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 110289 | 68241.3188 | 20 | 25.7417 | 0 | 0.50833 | 5 | 5 | 17060.3297 | 51180.9891 | 75%
|  |  | SUBTOTAL SERVICES | 34% | 70.125 | 110289 | 7734016.125
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 110289
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 110289
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 110289
|  |  | E1090 - OTHER EQUIPMENT |  |  | 110289
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 110289
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 110289
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 110289
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 110289
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 110289
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 110289 | 227471.0625 | 30 | 3.5 | 26.5 | 0.75 | 22.5 | 30 | 227471.0625 | 0 | 0%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 110289 | 113735.5312 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 28433.8828 | 85301.6484 | 75%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 110289 | 113735.5312 | 30 | 3.5 | 26.5 | 0.75 | 22.5 | 30 | 113735.5312 | 0 | 0%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 110289 | 113735.5312 | 30 | 3.5 | 26.5 | 0.75 | 22.5 | 30 | 113735.5312 | 0 | 0%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 110289 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 110289
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 110289 | 22747106.25 | [7 empty] | 3133294.63 | 13.77%
100%
Note on J41: Tessier, Matthew: No Survey Data
Note on J42: Tessier, Matthew: No Survey Data

## Master File (Interior)
Mount Vernon
School Code: | 570
NPS Code: | 85
Street: | 142 Mt. Vernon Pl.
City/Town: | Newark,
Database ID: | 72
Total size (gsf):
ROOM INFORMATION | [12 empty] | 47.0735 | Ave Condition | 0.51912 | [6 empty] | 17.473 | Ave Condition | 0.46081 | [5 empty] | 10.8056 | Ave Condition | 0.51389 | [6 empty] | 17.6286 | Ave Condition | 0.58571 | [6 empty] | 22.5 | Ave Condition | 0.50694 | [6 empty] | 48.4571 | Ave Condition | 0.57857 | [6 empty] | 23.3864 | Ave Condition | 0.51136 | [6 empty] | 21.2778 | Ave Condition | 0.58333 | [6 empty] | 21.2778 | Ave Condition | 0.58333 | [5 empty] | Average Age | 30 | Ave Condition | 0.5 | [6 empty] | 22.4286 | Ave Condition | 0.53571 | [6 empty] | 7.5 | Ave Condition | 0.75 | [6 empty] | 8.9194 | Ave Condition | 0.69355 | [6 empty] | 28.4833 | Ave Condition | 0.51667 | [6 empty] | 28.8103 | Ave Condition | 0.3431 | [6 empty] | 8.1 | Ave Condition | 0.68 | [6 empty] | 19.625 | Ave Condition | 0.625 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 10 | Ave Condition | 0.5 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [7 empty] | Ceiling Finish | [8 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [8 empty] | Plumbing Fixtures - Urinals | [8 empty] | Plumbing Fixtures - Showers | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
6239 | 2 | Electrical Room | Basement | A | Support |  |  | 356 | N/A
6240 | LL101 | Resource Room | Basement | A | Administration |  |  | 344 | 9' 3"
6241 | LL102 | Music | Basement | A | Visual & Performing Arts |  |  | 1060 | 9' 3" | Plaster Partitions/on CMU Back-up Wall | 0 | 15 | 7.5 | Very Good | 0.9 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls | 10+ | 10 | Poor | 0.25 |  |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 |  |  | Glued on | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | [12 empty] | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  | Duct work supply diffusers | [25 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 2CPU | [106 empty] | Present
6242 | LL103 | Dance | Basement | A | Visual & Performing Arts |  |  | 897 | 9' 3" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Ceiling mounted diffusers | [25 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 1CPU | [106 empty] | Present - Present
6243 | LL104 | Classroom | Basement | A | General Classroom |  |  | 835 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6244 | LL105 | Resource Room | Basement | A | Administration |  |  | 326 | 9' 3" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 | [11 empty] | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Ceiling mounted diffusers | [25 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 3CPU | [106 empty] | Present - Present - Present
6245 | LL106 | Resource Room | Basement | A | Administration |  |  | 326 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6246 | LL107 | Computer Lab | Basement | A | Technological Literacy |  |  | 847 | 9' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6247 | LL108 | Parent Liaison | Basement | A | Administration |  |  | 825 | N/A
6248 | LL109 | Site coordinator office | Basement | A | Administration |  |  | 158 | N/A
6249 | UN-1 | Electrical Room | Basement | A | Support |  |  | 115 | N/A
6250 | UN-2 | Boiler Room | Basement | A | Support |  |  | 1960 | N/A
6251 | UN-3 | Storage | Basement | A | Support |  |  | 59 | N/A
6252 | UN-4 | Storage | Basement | A | Support |  |  | 574 | N/A
6253 | UN-5 | Custodial office | Basement | A | Support |  |  | 264 | N/A
6254 | UN-6 | Storage | Basement | A | Support |  |  | 53 | N/A
6255 | UN-7 | Girls' Water Closet | Basement | A | Support |  |  | 114 | N/A | [59 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
6256 | UN-8 | Boys\' Water Closet | Basement | A | Support |  |  | 114 | N/A | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  | Mosaic | Painted Walls with Wainscot | 10+ | 10 | Fair | 0.5 |  |  | Glazed brick wainscot | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 46 | 60 | 53 | Fair | 0.5 |  |  |  | In-Counter Lavatories | 16 | 21 | 18.5 | Fair | 0.5 | 1 |  |  | Floor Mounted Flush Valve | 16 | 21 | 18.5 | Fair | 0.5 | 1 |  |  | Wall Hung | 16 | 21 | 18.5 | Fair | 0.5 | 2 | [20 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | [37 empty] | Present - Present - Present - Present
6257 | UN-9 | Music Storage | Basement | A | Visual & Performing Arts |  |  | 65 | N/A
6258 | UN-10 | Music Storage | Basement | A | Visual & Performing Arts |  |  | 62 | N/A
6259 | UN-11 | Storage | Basement | A | Administration |  |  | 23 | N/A
6260 | UN-12 | Storage | Basement | A | Administration |  |  | 8 | N/A
6261 | UN-13 | Storage | Basement | A | Administration |  |  | 28 | N/A
6262 | UN-14 | Storage | Basement | A | Support |  |  | 141 | N/A
6263 | UN-15 | Storage | Basement | A | Support |  |  | 84 | N/A
6264 | UN-16 | Storage | Basement | A | Support |  |  | 20 | N/A
6265 | UN-17 | Storage | Basement | A | Support |  |  | 77 | N/A
6266 | UN-18 | Storage | Basement | A | Support |  |  | 23 | N/A
6267 | UN-19 | Custodial Closet | Basement | A | Support |  |  | 120 | N/A
6268 | UN-20 | Water Closet | Basement | A | Support |  |  | 115 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Plaster | [32 empty] | 2 | [8 empty] | 2 | [8 empty] | 2
6269 | 101 | ESL | 1st Floor | A | Small Group Instruction |  |  | 1177 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [56 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 16 | 21 | 18.5 | Fair | 0.5 |  |  | Ducted HVAC self contained | [16 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 | [72 empty] | Present
6270 | 102 | 1st Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 844 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6271 | 104 | 1st Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 1088 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6272 | 105 | Classroom | 1st Floor | A | General Classroom |  |  | 1223 | 10' 5" | [9 empty] | Carpet | [16 empty] | Acoustical Panel
6273 | 106 | 1st Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 818 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6274 | 107 | 1st Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 704 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6275 | 108 | 2nd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 795 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6276 | 108A | Social Worker | 1st Floor | A | Administration |  |  | 182 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6277 | 109 | Kindergarten | 1st Floor | A | Kindergarten Classroom |  |  | 998 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [30 empty] | Other (describe) | 30+ |  | 30 | Poor | 0.25 |  |  | Attach to sink | [9 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [27 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present
6278 | 110 | 2nd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 771 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6279 | 110A | Child Study Team | 1st Floor | A | Administration |  |  | 213 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6280 | 111 | Kindergarten | 1st Floor | A | Kindergarten Classroom |  |  | 1019 | 12' 4" | [9 empty] | Carpet | [16 empty] | Acoustical Panel
6281 | 112 | 3rd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 782 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6282 | 113 | 2nd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 810 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6283 | 114 | 3rd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 935 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6284 | 115 | 3rd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 767 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | Concealed spline, water damage | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [56 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [27 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present - Present
6285 | 115A | ESL | 1st Floor | A | Small Group Instruction |  |  | 227 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6286 | 116 | Classroom | 1st Floor | A | General Classroom |  |  | 895 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6287 | 117 | 3rd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 791 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6288 | 117A | ESL | 1st Floor | A | Small Group Instruction |  |  | 212 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6289 | 118 | 4th Grade Classroom | 1st Floor | A | General Classroom (Grades 4-5) |  |  | 765 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6290 | 119 | Classroom | 1st Floor | A | General Classroom |  |  | 790 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6291 | 121 | 6th Grade Classroom | 1st Floor | A | General Classroom (Grades 6-8) |  |  | 637 | 12' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6292 | 122 | Classroom | 1st Floor | A | General Classroom |  |  | 527 | 12' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6293 | 170 | Kindergarten | 1st Floor | A | Kindergarten Classroom |  |  | 1026 | 12' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6294 | 171 | Kindergarten | 1st Floor | A | Kindergarten Classroom |  |  | 1014 | 12' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6295 | 172 | Kindergarten | 1st Floor | B | Kindergarten Classroom |  |  | 1031 | 12' 5" | CMU Back-up Wall | 16 | 30 | 23 | Fair | 0.5 |  |  |  | Carpet | 16 | 20 | 18 | Fair | 0.5 |  |  |  | Painted Walls | 41004 | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 16 | 20 | 18 | Good | 0.75 |  |  |  | Concrete Block | 16 | 30 | 23 | Fair | 0.5 |  |  |  | In-Counter Lavatories | 16 | 21 | 18.5 | Good | 0.75 | 2 | [47 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 16 | 21 | 18.5 | Good | 0.75 |  |  |  | Other (describe) | 16 | 21 | 18.5 | Good | 0.75 |  |  | HVAC ducted | [25 empty] | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 | [72 empty] | Present - Present - Present - Present
6296 | 173 | Kindergarten | 1st Floor | A | Kindergarten Classroom |  |  | 1016 | 12 '5" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6297 | 174 | Art | 1st Floor | B | General Classroom |  |  | 1342 | 9' 5" | CMU Back-up Wall | 16 | 30 | 23 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 16 | 20 | 18 | Good | 0.75 |  |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Good | 0.75 |  |  |  | Wood/Metal Frame | 16 | 20 | 18 | Good | 0.75 |  |  |  | Concrete Block | 16 | 30 | 23 | Fair | 0.5 |  |  |  | In-Counter Lavatories | 16 | 21 | 18.5 | Fair | 0.5 | [48 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 16 | 21 | 18.5 | Good | 0.75 |  |  |  | Other (describe) | 16 | 21 | 18.5 | Good | 0.75 |  |  | Fan coil ducted HVAC | [25 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present - Present
6298 | UN-21 | Cafeteria | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 3973 | 16' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 |  |  | Limited ares of VAT | Painted Walls | 41004 | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [39 empty] | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 | [12 empty] | Wet Chemical | 16 | 21 | 18.5 | Good | 0.75 |  |  | Water type class 2A | [7 empty] | Present - Present - Present - Present - Present - Present | [134 empty] | Present - Present - Present - Present - Present - Present | [26 empty] | Present | [8 empty] | Present
6299 | UN-22 | Kitchen | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 1040 | 16' 10" | [9 empty] | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | 5 | [47 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Kitchen exhaust hood | [9 empty] | Wet Chemical | 30+ |  | 30 | Fair | 0.5 |  |  | Ansul type kitchen hood extinguisher | [7 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present - Present - Present - Present | [26 empty] | Present - Present | [8 empty] | Present
6300 | UN-23 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 408 | N/A
6301 | UN-24 | Faculty Room | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 103 | N/A
6302 | UN-25 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 69 | N/A
6303 | UN-26 | Boys' Water Closet | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 95 | N/A | [9 empty] | Ceramic Tile | [49 empty] | 2 | [8 empty] | 2 | [8 empty] | 2
6304 | UN-27 | Girls\' Water Closet | 1st Floor | A | Support |  |  | 95 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 2 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 3 | [8 empty] | 0 | [29 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | 0 | [26 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
6305 | UN-28 | Custodial Room | 1st Floor | A | Support |  |  | 132 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel
6306 | UN-29 | N/A | 1st Floor | A | N/A |  |  | 105 | N/A
6307 | UN-30 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 29 | N/A
6308 | UN-31 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 43 | N/A
6309 | UN-32 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 53 | N/A
6310 | UN-33 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 37 | N/A
6311 | UN-34 | N/A | 1st Floor | A | N/A |  |  | 213 | N/A
6312 | UN-35 | Auditorium | 1st Floor | A | Visual & Performing Arts |  |  | 5452 | 22' 3 | [9 empty] | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 |  |  |  | Painted Walls | 10+ | 10 | Good | 0.75 |  |  |  | Acoustical Panel | 41136 |  | 11.5 | Good | 0.75 |  |  | Concealed spline w/ plaster | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 |  |  | W/ Central HV diffusers | [25 empty] | Present - Present - Present - Present - Present - Present - Present
6313 | UN-36 | Men's Water Closet | 1st Floor | A | Support |  |  | 69 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 1
6314 | UN-37 | Women's Water Closet | 1st Floor | A | Support |  |  | 79 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
6315 | UN-38 | N/A | 1st Floor | A | N/A |  |  | 91 | N/A | [59 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6316 | UN-39 | Nurse\'s Office | 1st Floor | A | Health Services |  |  | 200 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | [37 empty] | Present - Present - Present - Present - Present - Present - Present | [134 empty] | Present - Present - Present - Present - Present - Present - Present
6317 | UN-40 | Exam Room | 1st Floor | A | Health Services |  |  | 259 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | [48 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 22 | 30 | 26 | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present - Present - Present - Present
6318 | UN-41 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 75 | N/A
6319 | UN-42 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 63 | N/A
6320 | UN-43 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 41 | N/A
6321 | UN-44 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 72 | N/A
6322 | UN-45 | Girls\' Locker Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 482 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ | 10 | Poor | 0.25 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Very Poor | 0.1 | [28 empty] | Present - Present - Present - Present - Present - Present - Present
6323 | UN-46 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 171 | N/A
6324 | UN-47 | Janitors closet | 1st Floor | A | Support |  |  | 43 | N/A
6325 | UN-48 | Gymnasium | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 4697 | 17' 10" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ | 10 | Fair | 0.5 |  |  | Plaster damage above wainscot | Suspended Acoustical | 16 | 21 | 18.5 | Fair | 0.5 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Good | 0.75 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | [12 empty] | Wet Chemical | 41136 |  | 11.5 | Good | 0.75 |  |  | Water class 2A | [7 empty] | Present - Present - Present - Present - Present - Present - Present | [134 empty] | Present - Present - Present - Present - Present - Present - Present
6326 | UN-49 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 542 | N/A
6327 | UN-50 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 143 | N/A
6328 | UN-51 | N/A | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 66 | N/A
6329 | UN-52 | N/A | 1st Floor | A | Visual & Performing Arts |  |  | 112 | N/A
6330 | UN-53 | N/A | 1st Floor | A | Visual & Performing Arts |  |  | 90 | N/A
6331 | UN-54 | N/A | 1st Floor | A | Visual & Performing Arts |  |  | 88 | N/A
6332 | UN-55 | N/A | 1st Floor | A | Visual & Performing Arts |  |  | 57 | N/A
6333 | UN-56 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 44 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6334 | UN-57 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 50 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Other (describe) | 16 | 20 | 18 | Poor | 0.25 | 0 |  | Concrete | Painted Walls with Wainscot | 10+ | 10 | Good | 0.75 | 0 |  |  | Drywall (Gypsum) | 16 | 21 | 18.5 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 16 | 20 | 18 | Good | 0.75 | 0 |  |  | Concrete Block | 16 | 30 | 23 | Fair | 0.5 | 0 | [8 empty] | 1 |  |  | Floor Mounted Flush Valve | 16 | 21 | 18.5 | Fair | 0.5 | 1 |  |  | Wall Hung | 16 | 21 | 18.5 | Fair | 0.5 | 0 | [29 empty] | Fluorescent Linear Surface Mount Fixture | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Other (describe) | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  | Toilet exhaust | [25 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0
6335 | UN-58 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 49 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6336 | UN-59 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 51 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6337 | UN-60 | Water Closet | 1st Floor | A | Administration |  |  | 23 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6338 | UN-61 | Vice Principal's Office | 1st Floor | A | Administration |  |  | 212 | N/A
6339 | UN-62 | Main Office | 1st Floor | A | Administration |  |  | 274 | N/A | CMU Back-up Wall | 16 | 30 | 23 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Good | 0.75 |  |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 |  |  | Glued on | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [57 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  | 2x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | [19 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [10 empty] | Present | [98 empty] | Present - Present - Present - Present - Present - Present - Present | Head end system
6340 | UN-63 | N/A | 1st Floor | A | N/A |  |  | 211 | N/A
6341 | UN-64 | Office Reception | 1st Floor | A | Administration |  |  | 73 | N/A
6342 | UN-65 | N/A | 1st Floor | A | Administration |  |  | 40 | N/A
6344 | UN-67 | Water Closet | 1st Floor | A | Administration |  |  | 51 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6345 | UN-68 | Office | 1st Floor | A | Administration |  |  | 111 | N/A
6346 | UN-69 | Storage | 1st Floor | A | Support |  |  | 149 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel
6347 | UN-70 | Water Closet | 1st Floor | A | Administration |  |  | 28 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6348 | UN-71 | Principal's Office | 1st Floor | A | Administration |  |  | 218 | N/A
6349 | UN-72 | Media Center | 1st Floor | A | Media Center |  |  | 1684 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Carpet | 20+ |  | 20 | Poor | 0.25 | 0 |  | Sub floor is loose and has dips | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Demountable/Folding. | 46 | 60 | 53 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 |  |  |  | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 |  |  | Class 2A | [7 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 5 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
6350 | UN-73 | Water Closet | 1st Floor | A | General Classroom |  |  | 25 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6351 | UN-74 | Water Closet | 1st Floor | A | General Classroom |  |  | 24 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6352 | UN-75 | N/A | 1st Floor | A | General Classroom |  |  | 28 | N/A
6353 | UN-76 | Storage | 1st Floor | A | Small Group Instruction |  |  | 113 | N/A
6354 | UN-77 | Storage | 1st Floor | A | Small Group Instruction |  |  | 94 | N/A
6355 | UN-78 | Storage | 1st Floor | A | Small Group Instruction |  |  | 75 | N/A
6356 | UN-79 | Women's Faculty Water Closet | 1st Floor | A | Faculty Support |  |  | 139 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
6357 | UN-80 | N/A | 1st Floor | A | N/A |  |  | 107 | N/A
6358 | UN-81 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 28 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6359 | UN-82 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 29 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6360 | UN-83 | Faculty Water Closet | 1st Floor | A | Faculty Support |  |  | 82 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
6361 | UN-84 | Faculty Lounge | 1st Floor | A | Faculty Support |  |  | 135 | N/A
6362 | UN-85 | N/A | 1st Floor | A | N/A |  |  | 21 | N/A
6363 | UN-86 | Stock Room A | 1st Floor | A | Support |  |  | 212 | N/A
6364 | UN-87 | N/A | 1st Floor | A | N/A |  |  | 31 | N/A
6365 | UN-88 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 35 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6366 | UN-89 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 27 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6367 | UN-90 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 25 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6368 | UN-91 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 28 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Ceramic Tile Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 1 | [8 empty] | 0 | [29 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Toilet exhaust, lots of dust | [25 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0
6369 | UN-92 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 26 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6370 | UN-93 | N/A | 1st Floor | A | Kindergarten Classroom |  |  | 43 | N/A
6371 | UN-94 | Water Closet | 1st Floor | A | Faculty Support |  |  | 38 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6372 | UN-95 | Water Closet | 1st Floor | A | Faculty Support |  |  | 41 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6373 | UN-96 | N/A | 1st Floor | A | Kindergarten Classroom |  |  | 38 | N/A
6374 | UN-97 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 38 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6375 | UN-98 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 25 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6376 | UN-99 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 41 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6377 | UN-100 | Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 25 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6378 | UN-101 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 29 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6379 | UN-102 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 39 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6380 | UN-103 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 26 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6381 | UN-104 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 33 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6382 | UN-105 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 28 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6383 | UN-106 | Water Closet | 1st Floor | A | Small Group Instruction |  |  | 30 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6384 | UN-107 | N/A | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 33 | N/A
6385 | UN-108 | Water Closet | 1st Floor | A | Small Group Instruction |  |  | 29 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6386 | UN-109 | N/A | 1st Floor | A | General Classroom |  |  | 30 | N/A
6387 | UN-110 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 26 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6388 | UN-111 | N/A | 1st Floor | A | General Classroom |  |  | 37 | N/A
6389 | UN-112 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 29 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6390 | UN-113 | Girls' Locker Room | 1st Floor | A | General Classroom (Grades 4-5) |  |  | 34 | N/A
6391 | UN-114 | Water Closet | 1st Floor | A | General Classroom |  |  | 26 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
6392 | UN-115 | N/A | 1st Floor | A | General Classroom (Grades 4-5) |  |  | 33 | N/A
6393 | 201 | Science Lab | 2nd Floor | A | Science (6-12) |  |  | 891 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [48 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [27 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 | [45 empty] | Present | [26 empty] | Present
6394 | 202 | 7th & 8th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 856 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [26 empty] | 0 | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [71 empty] | 0 | Present - Present
6395 | 203 | 7th & 8th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 838 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6396 | 203A | Storage | 2nd Floor | A | Support |  |  | 667 | N/A
6397 | 204 | 5th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 868 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6398 | 205 | 4th Grade Math/Science Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 900 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [48 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [27 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present - Present
6399 | 206 | Classroom | 2nd Floor | A | General Classroom |  |  | 892 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6400 | 207 | 4th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 910 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6401 | 208 | 5th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 837 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6402 | 209 | Classroom | 2nd Floor | A | General Classroom |  |  | 804 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [27 empty] | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present - Present - Present
6403 | 210 | Classroom | 2nd Floor | A | General Classroom |  |  | 856 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6404 | 211 | Classroom | 2nd Floor | A | General Classroom |  |  | 842 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6405 | 212 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 865 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6406 | 213 | Classroom | 2nd Floor | A | General Classroom |  |  | 836 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6407 | 214 | Technology Lab | 2nd Floor | A | Technological Literacy |  |  | 833 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [56 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | [19 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 |  | Moveable | [15 empty] | 26 | [72 empty] | Present - Present - Present - Present - Present
6408 | 215 | Classroom | 2nd Floor | A | General Classroom |  |  | 864 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present - Present - Present - Present - Present - Present
6409 | 216 | 7th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 826 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6410 | 217 | Classroom | 2nd Floor | A | General Classroom |  |  | 834 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6411 | 218 | Classroom | 2nd Floor | A | General Classroom |  |  | 825 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6412 | 219 | Classroom | 2nd Floor | A | General Classroom |  |  | 832 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6413 | 220 | Classroom | 2nd Floor | A | General Classroom |  |  | 871 | 12' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
6414 | 221 | Classroom | 2nd Floor | A | General Classroom |  |  | 819 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [48 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 |  | Moveable | [15 empty] | 4 | [72 empty] | Present - Present - Present - Present - Present - Present - Present
6415 | 222 | Classroom | 2nd Floor | A | General Classroom |  |  | 842 | 12' 4" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ | 10 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [48 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [26 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 | [71 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
6416 | UN-116 | Boys\' Water Closet | 2nd Floor | A | Support |  |  | 240 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Poor | 0.25 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 4 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 4 |  | 1out of service | Wall Hung | 30+ |  | 30 | Fair | 0.5 | 5 | [20 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Very Poor | 0.1 | [28 empty] | Present - Present - Present - Present - Present - Present - Present
6417 | UN-117 | Janitors closet | 2nd Floor | A | Support |  |  | 28 | N/A
6418 | UN-118 | Stockroom C | 2nd Floor | A | Support |  |  | 795 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel
6419 | UN-119 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 264 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 4 | [8 empty] | 5 | [8 empty] | 0
6420 | UN-120 | Janitors closet | 2nd Floor | A | Support |  |  | 22 | N/A
6421 | UN-121 | Faculty Room | 2nd Floor | A | Faculty Support |  |  | 199 | N/A
6422 | UN-122 | Faculty Water Closet | 2nd Floor | A | Faculty Support |  |  | 79 | N/A | [59 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
6423 | UN-123 | Men's Faculty Water Closet | 2nd Floor | A | Faculty Support |  |  | 230 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 2 | [8 empty] | 2 | [8 empty] | 2
6424 | UN-124 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 183 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 4 | [8 empty] | 4 | [8 empty] | 5
6425 | UN-125 | Janitors closet | 2nd Floor | A | Support |  |  | 28 | N/A
6426 | UN-126 | Girls\' Water Closet | 2nd Floor | A | Support |  |  | 226 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 4 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 6 | [29 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | [28 empty] | Present - Present - Present - Present - Present - Present - Present
6427 | UN-127 | N/A | 2nd Floor | A | N/A |  |  | 39 | N/A
6428 | UN-128 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 219 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 4 | [8 empty] | 5 | [8 empty] | 2
6429 | UN-129 | Janitors closet | 2nd Floor | A | Support |  |  | 28 | N/A
6430 | UN-130 | Women's Faculty Water Closet | 2nd Floor | A | Faculty Support |  |  | 229 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
6431 | UN-131 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 275 | N/A | [9 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [32 empty] | 4 | [8 empty] | 6 | [8 empty] | 0
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [7 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
30 | A | Original 1955 | 1st | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  | Mine cracks | Painted Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | [12 empty] | Other (describe) | 46 | 60 | 53 | Fair | 0.5 |  |  | Plaster /on CMU Backup Wall | [9 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  | 2x4 | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [19 empty] | Present
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
101 | B | Addition 1996 | 1st Floor | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Ceramic tile wainscot | Suspended Acoustical | 30+ | 30 | Fair | 0.5 |  |  | Glued-on | [9 empty] | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [12 empty] | Other (describe) | 0 | 15 | 7.5 | Good | 0.75 |  |  | 2-tier metal | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 0 | 7 | 3.5 | Good | 0.75 |  |  | Water based | [7 empty] | Present | [17 empty] | Present | [8 empty] | Present
102 | C | Original 1955 | 2nd Floor | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  | Ceramic tile wainscot | Suspended Acoustical | 30+ | 30 | Good | 0.75 | 0 |  | Glued-on | [6 empty] | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [8 empty] | 0 |  |  | Other (describe) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  | 2-tier metal | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  | Water based | [6 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [7 empty] | Ceiling Finish | [8 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
96 | A | Original 1955 | Basement-2nd | [6 empty] | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Steel Pan | 30+ |  | 30 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  | Acoustic panels glued at 2nd floor ceiling | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  | Concrete fillings at specific steps | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Labeled Metal/Metal Frames | 41070 |  | 8 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [37 empty] | Present | Motion detector
97 | B | Original 1955 | 1st-2nd | [6 empty] | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Steel Pan | 30+ |  | 30 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  | Acoustic panels glued at 2nd floor ceiling | Terrazzo | 30+ |  | 30 | Poor | 0.25 |  |  | Cracks and majority of treads filled in with concrete | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Labeled Metal/Metal Frames | 41070 |  | 8 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [37 empty] | Present | Motion detector
98 | C | Original 1955 | 1st-2nd | [6 empty] | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Steel Pan | 30+ |  | 30 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  | Acoustic panels glued at 2nd floor ceiling | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  | Concrete fillings at specific steps | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Labeled Metal/Metal Frames | 41070 |  | 8 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [37 empty] | Present | Motion detector
EXTERIORs INFORMATION

## Master File (Systems)
systems | Question | Value1 |  | Average1 | Value2 | Average2
Systems | Seg ID | 775 |  |  | 776
| Bldg.Phase | A |  |  | B
| Original | 1 |  |  | 0
| Addition | 0 |  |  | 1
| Year Built | 1955 |  |  | 1996
Domestic Water Heaters | Location | UN02
| Description | Fuel/Fired Water Heater
| Age | 41136 |  | 11.5
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | 4 hot water storage tanks 15 yrs old, fair. Copper piping
Sanitary Drainage | Location | Roof
| Description | Sanitary Drainage Piping Cleanouts
| Age | 60+ |  | 60
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Bathroom vent piping
Building Support (other) Plumbing Systems | Location | Roof
| Description | Stormwater Drainage Sump Pumps
| Age | 60+ |  | 60
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Building sump pump 15 yrs old, fair condition
Fuel Piping | Location | UN02
| Description | Gas Piping
| Age | 46 | 60 | 53
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fuel Pumps | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fuel Storage Tanks | Location | UN02
| Description | Above/ground
| Age | 16 | 30 | 23
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fuel Fired Boilers | Location | UN02
| Description | Gas/Fired Boilers
| Age | 0 | 15 | 7.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Condensate return poor condition
Furnaces | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Unit Ventilators | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fan Coil Units | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Water Chillers | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Cooling Towers | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Packaged Terminal Air Conditioner | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Hydronic Piping System | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Pumps | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Steam Piping System | Location | UN02
| Description | Two Pipe
| Age | 46 | 60 | 53
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Partially replaced with new piping 15yrs old.
HVAC Air Distribution | Location | Roof
| Description | Insulated Sheet Metal Ducts
| Age | 16 | 30 | 23
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Air Handling Units | Location | Roof
| Description | Package Rooftop Units (RTU)
| Age | 21 | 30 | 25.5
| Condition | Fair |  | 0.5
CheckBox
| Quantity | 1
Voltage
Power Output
Elec Power
| Notes | 1 in UN02 and 1 in UN04 15 yrs old fair condition
HVAC Fans | Location | Roof |  |  | Roof
| Description | Other (describe) |  |  | Other (describe)
| Age | 40+ |  | 40 | 41233 | 10.5
| Condition | Fair |  | 0.5 | Fair | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Roof exhaust fan |  |  | Roof exhaust fan
Fire/Suppression (Sprinklers), Water/Based | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire/Suppression (Standpipes), Water/Based | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Facility Power Generation, Packaged Generator Assemblies | Location | 2
| Description | Gas Engine Generators
| Age | 16 | 30 | 23
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | 2
| Description | D5010 120
| Age | 46 | 60 | 53
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Voice Communication Terminal Equipment | Location | UN02
| Description | PDX/Key Systems
| Age | 0 | 10 | 5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | Main office
| Description | Public Address and Mass Notification Systems
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Video Surveillance Systems | Location | Main lobby
| Description | Analog Video Recording Devices
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | UN05
| Description | Fire Alarm Annunciation Panels
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Value2 |  | Average2 | Exterior | Question | Value1 |  | Average1
Exterior | Seg ID | 938 |  |  | 952 |  |  | SiteElements | Seg ID | 245
| Bldg.Phase | A |  |  | B |  |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  |  | Addition | 0
| Year Built | 1955 |  |  | 1996 |  |  |  | Year Built | 1955
(Foundation) Walls for Subgrade Enclosures, Primary | Location | Typical |  |  | Typical |  |  | Roadways | Location | S/22
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place |  |  |  | Description | Asphalt (Bituminous)
| Age | 46 | 60 | 53 | 16 | 30 | 23 |  | Age | 0 | 7 | 3.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location | [6 empty] | Parking Lots | Location | S/22
| Description | [7 empty] | Description | Asphalt (Bituminous)
| Age | [7 empty] | Age | 0 | 7 | 3.5
| Condition | [7 empty] | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Standard Slabs On Grade, Primary | Location | Typical |  |  | Typical |  |  | Pedestrian Plazas and Walkways, Primary | Location | S/7, S/4
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place |  |  |  | Description | Concrete, CIP
| Age | 46 | 60 | 53 | 16 | 30 | 23 |  | Age | 30+ |  | 30
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Poor |  | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | Various cracks
Standard Slabs On Grade, Secondary | Location | [6 empty] | Pedestrian Plazas and Walkways, Secondary | Location | S/2
| Description | [7 empty] | Description | Concrete, CIP
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | Few nosings missing
Floor Construction, Primary | Location | Typical |  |  | Typical |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location | S/9
| Description | Concrete, CIP Beams and Slab |  |  | Concrete, CIP Beams and Slab |  |  |  | Description | Turf, Synthetic
| Age | 46 | 60 | 53 | 16 | 30 | 23 |  | Age | 0 | 7 | 3.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Floor Construction, Secondary | Location | [6 empty] | Athletic, Recreational, and Playfield Areas, Secondary | Location | S/10
| Description | [7 empty] | Description | Other (describe)
| Age | [7 empty] | Age | 0 | 7 | 3.5
| Condition | [7 empty] | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | Asphalt with Rubberized Paint
Roof Construction, Structural Frame, Primary | Location | Typical |  |  | Typical |  |  | Site Lighting, Primary | Location | Typical
| Description | Concrete, CIP |  |  | Steel Framing, w/ Steel Deck |  |  |  | Description | Pole Mounted H.I.D.
| Age | 46 | 60 | 53 | 16 | 30 | 23 |  | Age | 0 | 7 | 3.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Roof Construction, Structural Frame, Secondary | Location | [6 empty] | Site Lighting, Secondary | Location | Typical
| Description | [7 empty] | Description | Building Mounted H.I.D.
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | Mix of HID and Fluorescent
Exterior Walls / Exterior Assembly, Primary | Location | Typical |  |  | Typical |  |  | Playground Surface | Location | S/8, S/11
| Description | Other (describe) |  |  | Other (describe) |  |  |  | Description | Mulch, Synthetic
| Age | 46 | 60 | 53 | 16 | 30 | 23 |  | Age | 0 | 7 | 3.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Brick Veneer w/ CMU Back/up Wall |  |  | Brick Veneer w/ CMU Back/up Wall |  |  |  | Notes | Asphalt with Rubberized Paint (@S/12) 0/7 yrs / good condition
Exterior Walls / Exterior Assembly, Secondary | Location | [6 empty] | Playground Equipment | Location | S/8, S/11
| Description | [7 empty] | Description | Multi/Component Play Equipment Set
| Age | [7 empty] | Age | 0 | 7 | 3.5
| Condition | [7 empty] | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | B/Ball courts (@S/12) 0/7 yrs / good condition
Exterior Windows, Primary | Location | Typical |  |  | Typical |  |  | TCUs | Location
| Description | Aluminum, Double Hung |  |  | Aluminum, Casement |  |  |  | Description
| Age | 30+ |  | 30 | 16 | 21 | 18.5 |  | Age
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated) |  |  | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox |  |  |  | Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary | Location | Typical |  |  | Typical
| Description | Aluminum, Awning/Hopper |  |  | Aluminum, Awning/Hopper
| Age | 30+ |  | 30 | 16 | 21 | 18.5
| Condition | Fair |  | 0.5 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
| Description | Glass, Double Pane (Insulated) |  |  | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
| CheckBox | Screens, Insect
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location | Typical |  |  | Typical
| Description | Fiber Reinforced Panel (FRP) |  |  | Steel (Hollow)
| Age | 0 | 15 | 7.5 | 16 | 30 | 23
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location | Typical |  |  | Typical
| Description | Asphalt, Built Up |  |  | Asphalt, Built Up
| Age | 30+ |  | 30 | 16 | 21 | 18.5
| Condition | Fair |  | 0.5 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | With ballast
Roofing, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location | Typical |  |  | Typical
| Description | Aluminum |  |  | Aluminum
| Age | 30+ |  | 30 | 16 | 21 | 18.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location | Typical |  |  | Typical
| Description | Other (describe) |  |  | Other (describe)
| Age | 30+ |  | 30 | 16 | 21 | 18.5
| Condition | Fair |  | 0.5 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Cast iron / clogged at several drains |  |  | Stainless steel scuppers
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes