## FCI Summary
Building Name: | Newton Street | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 90964
Number of Floors: | B + 3
School Age (years): | 139
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 54.94%
Facility Condition = | VERY POOR
FCI Deficiency Cost = | 10307674.1086
FCI Replacement Cost = | 18761325
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 408
Historic 2005 LRFP Capacity = | 596
Adjusted 2012 Capacity = | 507
Recent Occupancy % = | 80.47%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 84%
Classroom Adequacy = | FAIR
Special Spaces Adequacy % Score = | 66.19%
Special Spaces Adequacy = | POOR

## Uniformat FCI
Building Name: |  | Newton Street | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 90964
Largest Floor Level Area: |  | 23312
Vertical FAR Ratio: |  | 3.902
School Age (years): |  | 139
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 1.8% | 3.7125 | 90964 | 337703.85 | 100 | 139 | 0 | 0.5 | 5 | 5 | 16885.1925 | 320818.6575 | 95%
|  |  | A1030 - SLAB ON GRADE | 1.5% | 3.0938 | 90964 | 281419.875 | 100 | 139 | 0 | 0.5 | 5 | 5 | 14070.9938 | 267348.8812 | 95%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 90964 | 412749.15 | 100 | 139 | 0 | 0.625 | 5 | 5 | 20637.4575 | 392111.6925 | 95%
|  |  | SUBTOTAL SUBSTRUCTURE | 5.5% | 11.3438 | 90964 | 1031872.875
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 90964 | 2063745.75 | 100 | 139 | 0 | 0.625 | 5 | 5 | 103187.2875 | 1960558.4625 | 95%
|  |  | B1020 - ROOF CONSTRUCTION | 2.5% | 5.1562 | 90964 | 469033.125 | 100 | 139 | 0 | 0.625 | 5 | 5 | 23451.6562 | 445581.4688 | 95%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 9.5% | 19.5938 | 90964 | 1782325.875 | 100 | 139 | 0 | 0.62971 | 5 | 5 | 89116.2938 | 1693209.5813 | 95%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 5.5% | 11.3438 | 90964 | 1031872.875 | 30 | 30 | 0 | 0.825 | 24.75 | 24.75 | 851295.1219 | 180577.7531 | 17.5%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 2% | 4.125 | 90964 | 375226.5 | 30 | 14.5833 | 15.4167 | 0.7 | 21 | 30 | 375226.5 | 0 | 0%
|  |  | SUBTOTAL SHELL | 30.5% | 62.9063 | 90964 | 5722204.125
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 90964 | 750453 | 60 | 56.125 | 3.875 | 0.43333 | 26 | 29.875 | 373663.0562 | 376789.9438 | 50.21%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 90964 | 281419.875 | 20 | 23.3714 | 0 | 0.37714 | 5 | 5 | 70354.9688 | 211064.9062 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 90964 | 750453 | 20 | 7.5 | 12.5 | 0.625 | 12.5 | 20 | 750453 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 90964 | 281419.875 | 30 | 139 | 0 | 0.5 | 5 | 5 | 46903.3125 | 234516.5625 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 4% | 8.25 | 90964 | 750453 | 10 | 11.1429 | 0 | 0.31286 | 5 | 5 | 375226.5 | 375226.5 | 50%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 90964 | 1125679.5 | 20 | 20.5882 | 0 | 0.36143 | 5 | 5 | 281419.875 | 844259.625 | 75%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 90964 | 1125679.5 | 30 | 29.4032 | 0.59677 | 0.33939 | 10.1818 | 10.7786 | 404441.3492 | 721238.1508 | 64.07%
|  |  | SUBTOTAL INTERIORS | 27% | 55.6875 | 90964 | 5065557.75
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 0.7% | 1.4438 | 90964 | 131329.275 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 131329.275 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 90964 | 281419.875 | 60 | 22.8912 | 37.1088 | 0.60288 | 36.1727 | 60 | 281419.875 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 90964 | 243897.225 | 60 | 3.5 | 56.5 | 0.75 | 45 | 60 | 243897.225 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 90964 | 225135.9 | 60 | 60 | 0 | 0.25 | 15 | 15 | 56283.975 | 168851.925 | 75%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 90964 | 93806.625 | 30 | 53 | 0 | 0.25 | 5 | 5 | 15634.4375 | 78172.1875 | 83.33%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 3.2% | 6.6 | 90964 | 600362.4 | 60 | 38 | 22 | 0.25 | 15 | 37 | 370223.48 | 230138.92 | 38.33%
|  |  | D3020 - BOILERS | 2.5% | 5.1562 | 90964 | 469033.125 | 60 | 60 | 0 | 0.25 | 15 | 15 | 117258.2812 | 351774.8438 | 75%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4.5% | 9.2812 | 90964 | 844259.625 | 40 | 46.6667 | 0 | 0.2 | 5 | 5 | 105532.4531 | 738727.1719 | 87.5%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4.5% | 9.2812 | 90964 | 844259.625 | 40 | 25.2143 | 14.7857 | 0.50286 | 20.1143 | 34.9 | 736616.5228 | 107643.1022 | 12.75%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 0% | 0 | 90964 | 0 | 40 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | #DIV/0!
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.8% | 3.7125 | 90964 | 337703.85 | 20 | 0 | 20 | 0 | 0 | 20 | 337703.85 | 0 | 100%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 90964 | 187613.25 | 20 | 0 | 20 | 0 | 0 | 20 | 187613.25 | 0 | 100%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 90964 | 37522.65 | 20 | 13.8333 | 6.1667 | 0.66667 | 13.3333 | 19.5 | 36584.5837 | 938.0663 | 2.5%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 90964 | 243897.225 | 60 | 60 | 0 | 0.25 | 15 | 15 | 60974.3063 | 182922.9188 | 75%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 90964 | 1313292.75 | 30 | 17.8793 | 12.1207 | 0.51149 | 15.3448 | 27.4655 | 1202342.1556 | 110950.5944 | 8.448%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 90964 | 562839.75 | 20 | 11.4286 | 8.5714 | 0.60884 | 12.1769 | 20 | 562839.75 | 0 | 0%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 90964 | 56283.975 | 20 | 41.5 | 0 | 0.21667 | 5 | 5 | 14070.9937 | 42212.9812 | 75%
|  |  | SUBTOTAL SERVICES | 34.5% | 71.1562 | 90964 | 6472657.125
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 90964
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 90964
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 90964
|  |  | E1090 - OTHER EQUIPMENT |  |  | 90964
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 90964
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 90964
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 90964
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 90964
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 90964
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 90964 | 187613.25 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 46903.3125 | 140709.9375 | 75%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 90964 | 93806.625 | 30 | 0 | 30 | 0 | 0 | 30 | 93806.625 | 0 | 0%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 90964 | 93806.625 | 30 | 11.5 | 18.5 | 0.9 | 27 | 30 | 93806.625 | 0 | 0%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 90964 | 93806.625 | 30 | 11.5 | 18.5 | 0.75 | 22.5 | 30 | 93806.625 | 0 | 0%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 90964 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 90964
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 90964 | 18761325 | [7 empty] | 10307674.1086 | 54.94%
100%
Note on J41: Tessier, Matthew: No Survey Data
Note on J42: Tessier, Matthew: No Survey Data
Note on J59: Tessier, Matthew: No Survey Data

## Master File (Interior)
Newton Street
School Code: | 580
NPS Code: | 86
Street: | 150 Newton St.
City/Town: | Newark,
Database ID: | 13
Total size (gsf):
ROOM INFORMATION | [11 empty] | Average Age | 57.5143 | Ave Condition | 0.14857 | [5 empty] | Average Age | 20.5882 | Ave Condition | 0.36143 | [5 empty] | Average Age | 11.1429 | Ave Condition | 0.31286 | [5 empty] | Average Age | 29.4032 | Ave Condition | 0.33939 | [6 empty] | 23.3714 | Ave Condition | 0.37714 | [6 empty] | 56.125 | Ave Condition | 0.43333 | [5 empty] | Average Age | 27.2727 | Ave Condition | 0.47273 | [6 empty] | 22.5 | Ave Condition | 0.625 | [6 empty] | 16.6 | Ave Condition | 0.7 | [5 empty] | Average Age | 23.8333 | Ave Condition | 0.71667 | [6 empty] | 24.25 | Ave Condition | 0.5 | [6 empty] | 7.5 | Ave Condition | 0.625 | [5 empty] | Average Age | 12.1379 | Ave Condition | 0.53448 | [5 empty] | Average Age | 30 | Ave Condition | 0.33333 | [5 empty] | Average Age | 30 | Ave Condition | 0.47 | [6 empty] | 20.4286 | Ave Condition | 0.53571 | [6 empty] | 13.8333 | Ave Condition | 0.66667 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 10 | Ave Condition | 0.5119 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [8 empty] | Plumbing Fixtures - Urinals | [8 empty] | Plumbing Fixtures - Showers | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
1265 | 2 | Classroom | Basement | A | General Classroom |  |  | 792 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1266 | 3 | Parent Room | Basement | A | Administration |  |  | 836 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1267 | UN-01 | Custodial Closet | Basement | A | Support |  |  | 76 | 9' 2" | [9 empty] | Unfinished | [17 empty] | Plaster
1268 | UN-02 | Custodial Closet | Basement | A | Support |  |  | 12 | 7' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
1269 | UN-03 | Food Prep | Basement | B | Food Service/Assembly (K-8) |  |  | 812 | N/A | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Very Poor | 0.1 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Other (describe) | 60+ |  | 60 | Poor | 0.25 | 0 |  | Brick painted | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | [36 empty] | 0 | [11 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Kit exhaust hood | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 |  | Exit on floor no mount | [6 empty] | 0 | Present | Heat detector | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [10 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A | [69 empty] | 0 | Present | [25 empty] | 0 | [8 empty] | 0
1270 | UN-04 | Art | Basement | B | Visual & Performing Arts |  |  | 876 | 9' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 | [6 empty] | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Brick Painted | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | [36 empty] | 0 | [11 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 4 | [6 empty] | 0 | [98 empty] | 0 | Present | Clock not working
1271 | UN-05 | Art Storage | Basement | A | Visual & Performing Arts |  |  | 126 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1272 | UN-06 | Storage | Basement | A | Support |  |  | 179 | 9' 2" | [9 empty] | Epoxy | [17 empty] | Plaster
1273 | UN-07 | Storage | Basement | A | Support |  |  | 8 | N/A
1274 | UN-08 | Water Closet | Basement | A | Support |  |  | 63 | 7' 6" | [9 empty] | Epoxy | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1275 | UN-09 | Boiler Room | Basement | A | Support |  |  | 2542 | N/A
1276 | UN-10 | Boiler Room | Basement | A | Support |  |  | 946 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
1277 | UN-11 | Service | Basement | A | Support |  |  | 422 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
1278 | UN-12 | Storage | Basement | A | Food Service/Assembly (K-8) |  |  | 82 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
1279 | UN-13 | Cafeteria | Basement | B | Food Service/Assembly (K-8) |  |  | 2633 | 9' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Other (describe) | 20+ |  | 20 | Poor | 0.25 | 0 |  | Painted concrete | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [38 empty] | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Fair | 0.5 | 0 | [11 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 | 0 | [8 empty] | 0 | Present | Smoke | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0 | Present | Speaker | [24 empty] | 0 | [8 empty] | 0
1280 | UN-14 | Girls' Water Closet | Basement | A | Support |  |  | 443 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 5 | [8 empty] | 9 | [8 empty] | 0
1281 | UN-15 | N/A | Basement | A | N/A |  |  | 273 | N/A
1282 | UN-16 | Custodial Office | Basement | A | Support |  |  | 319 | 9' 2" | [9 empty] | Unfinished | [17 empty] | Plaster
1283 | UN-17 | N/A | Basement | A | N/A |  |  | 26 | N/A
1284 | UN-18 | Storage | Basement | A | Media Center |  |  | 109 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1285 | UN-19 | Office | Basement | A | Media Center |  |  | 121 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1286 | UN-20 | Library | Basement | B | Media Center |  |  | 980 | 9' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Very Poor | 0.1 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Vented duct | Window Mounted | 30+ |  | 30 | Fair | 0.5 | 0 |  | window ac | [6 empty] | 0 | [8 empty] | 0 | Present | Strobe | [6 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 5 | [6 empty] | 0 | [26 empty] | 5 |  | Desktops | [69 empty] | 0 | Present | Speaker and clock
1287 | UN-21 | Boys' Water Closet | Basement | A | Support |  |  | 331 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 9 | [8 empty] | 8
1288 | UN-22 | Custodial Closet | Basement | A | Support |  |  | 12 | 7' 0" | [9 empty] | Unfinished | [17 empty] | Plaster
1289 | UN-23 | N/A | Basement | A | N/A |  |  | 1010 | N/A
1290 | UN-24 | Storage | Basement | A | Support |  |  | 18 | 7' 0" | [9 empty] | Wood | [17 empty] | Plaster
1291 | UN-25 | N/A | Basement | A | N/A |  |  | 227 | N/A
1292 | UN-26 | Storage | Basement | A | Support |  |  | 741 | 6' 10" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1293 | UN-27 | Storage | Basement | A | Support |  |  | 656 | 6' 10" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1294 | UN-28 | Storage | Basement | A | Support |  |  | 655 | 6' 10" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1295 | UN-29 | Storage | Basement | A | Support |  |  | 242 | 6' 10" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1296 | 107 | 1st Grade Classroom | 1st Floor | B | General Classroom (Grades 1-3) |  |  | 825 | 12' 2" | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  | water damage exterior window | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [26 empty] | 3 |  | Desktops | [69 empty] | 0 | Present | Speaker and clock
1297 | 112A | Resource Room | 1st Floor | A | Administration |  |  | 101 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1298 | 113 | Child Study Team | 1st Floor | A | Administration |  |  | 451 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1299 | UN-30 | N/A | 1st Floor | A | N/A |  |  | 140 | N/A
1300 | UN-31 | Custodial Closet | 1st Floor | A | Support |  |  | 11 | 7' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
1301 | UN-32 | Classroom | 1st Floor | A | General Classroom |  |  | 788 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1302 | UN-33 | Classroom | 1st Floor | A | General Classroom |  |  | 815 | 12' 2" | [9 empty] | Wood | [17 empty] | Plaster
1303 | UN-34 | Classroom | 1st Floor | B | General Classroom |  |  | 809 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick painted | Wood | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Very Poor | 0.1 | 0 |  |  | Wood/Wood Frame | 16 | 20 | 18 | Poor | 0.25 | 0 |  | Peeling paint | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 | [6 empty] | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [26 empty] | 3 |  | Desktops | [69 empty] | 0 | Present
1304 | UN-35 | Classroom | 1st Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1305 | UN-36 | Classroom | 1st Floor | B | General Classroom |  |  | 650 | 12' 2 | Plaster Partitions/Metal Stud Framing | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | Peeling paint | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 |  |  | Sink and toilet (2) | [45 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [26 empty] | 3 |  | Desktops | [69 empty] | 0 | Present
1306 | UN-37 | Boys' Water Closet | 1st Floor | A | General Classroom |  |  | 47 | N/A | [60 empty] | 1 | [8 empty] | 2 | [8 empty] | 0
1307 | UN-38 | Girls' Water Closet | 1st Floor | A | General Classroom |  |  | 38 | N/A | [60 empty] | 1 | [8 empty] | 2 | [8 empty] | 0
1308 | UN-39 | Storage | 1st Floor | A | General Classroom |  |  | 44 | N/A
1309 | UN-40 | Storage | 1st Floor | A | General Classroom |  |  | 18 | N/A
1310 | UN-41 | Girls' Water Closet | 1st Floor | A | Support |  |  | 191 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1311 | UN-42 | Classroom | 1st Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1312 | UN-43 | Auditorium | 1st Floor | B | Food Service/Assembly (K-8) |  |  | 4274 | 23' 0 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Very Poor | 0.1 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [44 empty] | 0 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 2x4, stage lights | [6 empty] | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator, floor mount vent, return vent Ceiling | [6 empty] | 0 |  |  | Wet Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | Present | Pull down, strobe, smoke | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0 | Present | Speakers, clock not working | [24 empty] | 0 | [8 empty] | 0
1313 | UN-44 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 72 | 8' 0" | [9 empty] | Wood | [17 empty] | Plaster
1314 | UN-45 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 181 | N/A
1315 | UN-46 | N/A | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 59 | N/A
1316 | UN-47 | Classroom | 1st Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Wood | [17 empty] | Plaster
1317 | UN-48 | Boys' Water Closet | 1st Floor | A | Support |  |  | 200 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 2 | [8 empty] | 4
1318 | UN-49 | Women's Water Closet | 1st Floor | A | Faculty Support |  |  | 149 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 4 | [8 empty] | 0
1319 | UN-50 | Custodial Closet | 1st Floor | A | Support |  |  | 7 | 8' 9" | [9 empty] | Unfinished | [17 empty] | Plaster
1320 | UN-51 | N/A | 1st Floor | A | N/A |  |  | 9 | N/A
1321 | UN-52 | Water Closet | 1st Floor | A | Faculty Support |  |  | 115 | 9' 6" | [9 empty] | Epoxy | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1322 | UN-53 | Storage | 1st Floor | A | Administration |  |  | 77 | 12' 2" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1323 | UN-54 | Administration Office | 1st Floor | A | Administration |  |  | 661 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Very Poor | 0.1 | 0 |  |  | Other (describe) | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | Wood | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Very Poor | 0.1 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Very Poor | 0.1 | [48 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Smoke | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0 | Present | Speaker, clock not working
1324 | UN-55 | Principal's Office | 1st Floor | A | Administration |  |  | 643 | 12' 2" | [9 empty] | Carpet | [17 empty] | Unfinished Ceiling
1325 | UN-56 | Storage | 1st Floor | A | Administration |  |  | 11 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1326 | UN-57 | Office | 1st Floor | A | Administration |  |  | 190 | 12' 2" | [9 empty] | Carpet | [17 empty] | Unfinished Ceiling
1327 | UN-58 | Main Office | 1st Floor | A | Administration |  |  | 408 | 9' 6 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | 0 |  | 2x4 | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 2x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam Radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Fire panel, strobe, pull, smoke | [6 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 2 | [6 empty] | 0 | [98 empty] | 0 | Present | Public address paging panel
1328 | UN-59 | Storage | 1st Floor | A | Administration |  |  | 24 | 9' 6" | [9 empty] | Wood | [17 empty] | Plaster
1329 | UN-60 | N/A | 1st Floor | A | Health Services |  |  | 24 | N/A
1330 | UN-61 | N/A | 1st Floor | A | Health Services |  |  | 111 | N/A
1331 | UN-62 | Health Office | 1st Floor | A | Health Services |  |  | 175 | N/A | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Very Poor | 0.1 | [36 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 | [6 empty] | Fair | 0.5 | 0 |  | Steam radiator | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 | [6 empty] | 0 | [98 empty] | 0 | Present | Speaker and Clock
1332 | UN-63 | Storage | 1st Floor | A | General Classroom |  |  | 58 | N/A
1333 | UN-64 | N/A | 1st Floor | A | Administration |  |  | 183 | N/A
1334 | UN-65 | Storage | 1st Floor | A | Administration |  |  | 58 | N/A
1335 | UN-66 | Storage | 1st Floor | A | Administration |  |  | 14 | N/A
1336 | UN-67 | Storage | 1st Floor | A | General Classroom |  |  | 9
1337 | UN-68 | Classroom | 1st Floor | A | General Classroom |  |  | 654 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1338 | UN-69 | N/A | 1st Floor | A | General Classroom |  |  | 3 | N/A
1339 | UN-70 | N/A | 1st Floor | A | General Classroom |  |  | 3 | N/A
1340 | UN-71 | Classroom | 1st Floor | A | General Classroom |  |  | 653 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Very Poor | 0.1 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Painted Wood | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | [5 empty] | 0 |  | Wood Panel | [54 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 | [6 empty] | Fair | 0.5 | 0 |  | Steam Radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Smoke | [6 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [26 empty] | 3 |  | Desktops | [69 empty] | 0 | Present | Clock and speaker
1341 | UN-72 | N/A | 1st Floor | A | General Classroom |  |  | 47 | N/A
1342 | UN-73 | N/A | 1st Floor | A | General Classroom |  |  | 41 | N/A
1343 | UN-74 | Water Closet | 1st Floor | A | Administration |  |  | 33 | 10' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1344 | 203 | Classroom | 2nd Floor | A | General Classroom |  |  | 788 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1345 | 210 | Social Worker | 2nd Floor | A | Administration |  |  | 661 | 11' 8" | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | Painted Wood | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Poor | 0.25 |  |  | 1x4 | [45 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Radiator heat, return air vent grills | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Smoke | [6 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 Ethernet jack, 2 pc | [6 empty] | 0 | [98 empty] | 0 | Present | Speaker and clock
1346 | 212 | Classroom | 2nd Floor | A | General Classroom |  |  | 653 | 11' 8" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1347 | 212A | Crisis Room | 2nd Floor | A | Administration |  |  | 101 | 11' 8" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1348 | 213 | Classroom | 2nd Floor | A | General Classroom |  |  | 652 | 11' 8" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1349 | 215 | Attendance Counselor | 2nd Floor | A | Administration |  |  | 115 | N/A
1350 | UN-75 | Storage | 2nd Floor | A | Support |  |  | 140 | 12' 2" | [9 empty] | Wood | [17 empty] | Plaster
1351 | UN-76 | N/A | 2nd Floor | A | N/A |  |  | 11 | N/A
1352 | UN-77 | Classroom | 2nd Floor | A | General Classroom |  |  | 815 | 12' 2" | [9 empty] | Wood | [17 empty] | Plaster
1353 | UN-78 | Classroom | 2nd Floor | B | General Classroom |  |  | 809 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Painted Wood | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [7 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 5 | [6 empty] | 0 |  | N/A | [8 empty] | N/A | [8 empty] | N/A | [6 empty] | 5 |  | Desktops | [69 empty] | 0 | Present
1354 | UN-79 | Classroom | 2nd Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1355 | UN-80 | Classroom | 2nd Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1356 | UN-81 | N/A | 2nd Floor | A | N/A |  |  | 63 | N/A
1357 | UN-82 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 191 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
1358 | UN-83 | Computer Lab | 2nd Floor | B | Technological Literacy |  |  | 825 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Very Poor | 0.1 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam Radiator | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 2 window ac | [6 empty] | 0 |  | N/A | [6 empty] | 0 | Present | [7 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 24 pc, 1 IDF switch | [6 empty] | 0 |  | N/A | [6 empty] | 1 |  | Present | [8 empty] | N/A | [6 empty] | 24 |  | Desktops | [69 empty] | 0 | Present
1359 | UN-84 | Upper Auditorium | 2nd Floor | B | Food Service/Assembly (K-8) |  |  | 2444 | N/A | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [10 empty] | N/A | [33 empty] | 0 |  | N/A | [9 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [98 empty] | 0 | Present | [25 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A
1360 | UN-85 | N/A | 2nd Floor | A | N/A |  |  | 181 | N/A
1361 | UN-86 | Classroom | 2nd Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Wood | [17 empty] | Plaster
1362 | UN-87 | Classroom | 2nd Floor | B | General Classroom |  |  | 825 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted |  |  |  |  | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 | [6 empty] | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 | [6 empty] | Fair | 0.5 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [26 empty] | 3 |  | Desktop | [69 empty] | 0 | Present
1363 | UN-88 | Boys\' Water Closet | 2nd Floor | B | Support |  |  | 200 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Ceramic Tile Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Acoustical Panel | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 2x4 | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | 2 |  | 4 | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 2 |  | 4 | Wall Hung | 30+ |  | 30 | Fair | 0.5 | 3 |  | 4 | [15 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 2x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Strobe | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
1364 | UN-89 | Women's Water Closet | 2nd Floor | A | Faculty Support |  |  | 149 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 3 | [8 empty] | 0
1365 | UN-90 | Custodial Closet | 2nd Floor | A | Support |  |  | 7 | 8' 9" | [9 empty] | Unfinished | [17 empty] | Plaster
1366 | UN-91 | N/A | 2nd Floor | A | N/A |  |  | 9 | N/A
1367 | UN-92 | Storage | 2nd Floor | A | General Classroom |  |  | 132 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1368 | UN-93 | Classroom | 2nd Floor | A | General Classroom |  |  | 661 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1369 | UN-94 | N/A | 2nd Floor | A | N/A |  |  | 190 | N/A
1370 | UN-95 | N/A | 2nd Floor | A | N/A |  |  | 408 | N/A
1371 | UN-96 | N/A | 2nd Floor | A | N/A |  |  | 24 | N/A
1372 | UN-97 | N/A | 2nd Floor | A | N/A |  |  | 24 | N/A
1373 | UN-98 | Staff Louge | 2nd Floor | A | Faculty Support |  |  | 265 | 11' 4 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1374 | UN-99 | N/A | 2nd Floor | A | N/A |  |  | 27 | N/A
1375 | UN-100 | Storage | 2nd Floor | A | General Classroom |  |  | 58 | 11' 6" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1376 | UN-101 | Storage | 2nd Floor | A | General Classroom |  |  | 58 | N/A | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1377 | UN-102 | Storage | 2nd Floor | A | General Classroom |  |  | 14 | N/A
1378 | UN-103 | Art Classroom | 2nd Floor | A | Visual & Performing Arts |  |  | 654 | 11' 8 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Very Poor | 0.1 | 0 |  |  | Other (describe) | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | Painted wood, peeling paint | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 | [10 empty] | N/A | [45 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Radiator | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | [6 empty] | 0 | Present | Smoke | [6 empty] | 0 |  | N/A | [6 empty] | 0 |  | N/A | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 |  | N/A | [8 empty] | N/A | [8 empty] | N/A | [8 empty] | 3 | [69 empty] | 0 | Present
1379 | UN-104 | Storage | 2nd Floor | A | General Classroom |  |  | 9 | N/A
1380 | UN-105 | Storage | 2nd Floor | A | General Classroom |  |  | 3 | N/A
1381 | UN-106 | Storage | 2nd Floor | A | General Classroom |  |  | 3 | N/A
1382 | UN-107 | N/A | 2nd Floor | A | General Classroom |  |  | 47 | N/A
1383 | UN-108 | Storage | 2nd Floor | A | General Classroom |  |  | 41 | N/A
1384 | UN-109 | Water Closet | 2nd Floor | A | Administration |  |  | 33 | 10' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1385 | 301 | Classroom | 3rd Floor | B | General Classroom |  |  | 809 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiatorN/A | Window Mounted | 30+ |  | 30 | Fair | 0.5 | 0 |  | 2 ac | [6 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 5 | [6 empty] | 0 | [8 empty] | 1 |  | Mobile | [15 empty] | 5 |  | Desktops | [69 empty] | 0 | Present
1386 | 302 | Classroom | 3rd Floor | A | General Classroom |  |  | 815 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1387 | 303 | Classroom | 3rd Floor | A | General Classroom |  |  | 788 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1388 | 303A | Speech & Language | 3rd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 140 | 11' 4" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1389 | 304 | Classroom | 3rd Floor | B | General Classroom |  |  | 825 | 12' 2 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiators | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 5 | [6 empty] | 0 | [26 empty] | 5 |  | Desktops | [69 empty] | 0 | Present
1390 | 305 | Classroom | 3rd Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1391 | 306 | Classroom | 3rd Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Wood | [17 empty] | Plaster
1392 | 307 | Classroom | 3rd Floor | A | General Classroom |  |  | 825 | 12' 2" | [9 empty] | Wood | [17 empty] | Plaster
1393 | 308 | 4th Grade Classroom | 3rd Floor | B | General Classroom (Grades 4-5) |  |  | 825 | 12' 2 | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  | Peeling plaster | Painted Walls | 10+ |  | 10 | Very Poor | 0.1 | 0 |  | Peeling plaster | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [26 empty] | 3 |  | Desktops | [69 empty] | 0 | Present
1394 | 309 | Science Classroom | 3rd Floor | A | Science (6-12) |  |  | 661 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1395 | 310 | Science Classroom | 3rd Floor | A | Science (6-12) |  |  | 663 | 11' 8" | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed spline | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Very Poor | 0.1 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Radiator | Window Mounted | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  | window ac | [6 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Good | 0.75 | 0 |  | 2 | [6 empty] | 0 | [26 empty] | 2 |  | Desktops | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [26 empty] | 0 | Present | Speaker with clock
1396 | 311 | Classroom | 3rd Floor | A | General Classroom |  |  | 654 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1397 | 312 | Classroom | 3rd Floor | A | General Classroom |  |  | 653 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1398 | 312A | Office | 3rd Floor | A | Administration |  |  | 101 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1399 | 313 | 4th/5th Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 652 | 11' 8" | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Painted Wood | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Very Poor | 0.1 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Smoke and Heat | [6 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 5 | [6 empty] | 0 | [26 empty] | 5 |  | Desktops | [69 empty] | 0 | Present | Speaker w/ clock
1400 | 314 | Small Group Instruction | 3rd Floor | A | Small Group Instruction |  |  | 265 | 11' 8" | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Painted Wood | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Smoke and Heat | [6 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 3 | [6 empty] | 0 | [26 empty] | 3 |  | Desktops | [69 empty] | 0 | Present | Clock and speaker
1401 | 315 | N/A | 3rd Floor | A | N/A |  |  | 110 | N/A
1402 | UN-110 | N/A | 3rd Floor | A | N/A |  |  | 11 | N/A
1403 | UN-111 | Storage | 3rd Floor | A | Support |  |  | 63 | 7' 6" | [9 empty] | Unfinished | [17 empty] | Plaster
1404 | UN-112 | Girls\' Water Closet | 3rd Floor | B | Support |  |  | 191 | 13' 0 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Ceramic Tile | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Drywall (Gypsum)/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | 2 |  |  | Floor Mounted Flush Tank | 30+ |  | 30 | Fair | 0.5 | 3 | [8 empty] | 0 | [17 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Fair | 0.5 | 0 |  |  | Fluorescent Pendant Mount Fixture | 41136 |  | 11.5 | Poor | 0.25 | 0 |  | 1x4 | [6 empty] | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
1405 | UN-113 | Gym | 3rd Floor | B | Phys. Ed. (Gym + Storage) |  |  | 4067 | 18' 6 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Brick | [33 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Other (describe) | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 4x4 metal halide | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Steam Radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Strobe and smoke | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0 | Present | Fire exit light broken
1406 | UN-114 | Changing Room | 3rd Floor | B | Phys. Ed. (Gym + Storage) |  |  | 153 | 11' 1 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Very Poor | 0.1 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Other (describe) | 60+ |  | 60 | Poor | 0.25 | 0 |  | Plaster on brick | [33 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Panel Breaker Switching | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Steam radiator | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Strobe and smoke | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
1407 | UN-115 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 67 | N/A
1408 | UN-116 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 29 | N/A
1409 | UN-117 | Changing Room | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 181 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1410 | UN-118 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 200 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [32 empty] | 4 | [8 empty] | 3 | [8 empty] | 4
1411 | UN-119 | Men's Water Closet | 3rd Floor | A | Faculty Support |  |  | 149 | 14' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 2 | [8 empty] | 1
1412 | UN-120 | Custodial Closet | 3rd Floor | A | Support |  |  | 7 | 8' 9" | [9 empty] | Unfinished | [17 empty] | Plaster
1413 | UN-121 | Science Storage | 3rd Floor | A | Science (6-12) |  |  | 132 | N/A | [9 empty] | Wood | [17 empty] | Plaster
1414 | UN-122 | Storage | 3rd Floor | A | Support |  |  | 12 | 9' 11" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1415 | UN-123 | Science Storage | 3rd Floor | A | Science (6-12) |  |  | 191 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1416 | UN-124 | Administration Office | 3rd Floor | A | Administration |  |  | 408 | 11' 8 | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 | 0 |  | Brick Painted | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Painted Wood | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Poor | 0.25 | 0 | [56 empty] | Fluorescent Pendant Mount Fixture | 30+ |  | 30 | Poor | 0.25 | 0 |  | 1x4 | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Radiator | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | window ac | [6 empty] | 0 | [8 empty] | 0 | Present | Smoke and heat | [6 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 | [6 empty] | 0 | [98 empty] | 0 | Present | Speaker w/ clock
1417 | UN-125 | N/A | 3rd Floor | A | Administration |  |  | 24 | N/A
1418 | UN-126 | Storage | 3rd Floor | A | Small Group Instruction |  |  | 24 | N/A
1419 | UN-127 | N/A | 3rd Floor | A | N/A |  |  | 27 | N/A
1420 | UN-128 | Storage | 3rd Floor | A | General Classroom |  |  | 58 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1421 | UN-129 | Storage | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 58 | 11' 8" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1422 | UN-130 | Storage | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 14 | 8' 9" | [9 empty] | Wood | [17 empty] | Plaster
1423 | UN-131 | Storage | 3rd Floor | A | General Classroom |  |  | 9 | N/A
1424 | UN-132 | Storage | 3rd Floor | A | General Classroom |  |  | 3 | N/A
1425 | UN-133 | Storage | 3rd Floor | A | General Classroom |  |  | 3 | N/A
1426 | UN-134 | Storage | 3rd Floor | A | General Classroom |  |  | 91 | 11' 10" | [9 empty] | Wood | [17 empty] | Unfinished Ceiling
1427 | UN-135 | Water Closet | 3rd Floor | A | Administration |  |  | 33 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
1 | A | Main Entrance | 1st Floor | Was not surveyed | [83 empty] | 0 | [8 empty] | 0 | [17 empty] | 0 | [17 empty] | 0 | [8 empty] | 0
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
1 | A | North End | 3 | [6 empty] | Other (describe) | 20+ |  | 20 | Good | 0.75 | 0 |  | Painted concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  | Plaster | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [6 empty] | Good | 0.75 | 0 |  | Unknown type, 2 not in operation | [6 empty] | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1x4 | [6 empty] | 0 |  |  | Other (describe) | 30+ |  | 30 | Very Good | 0.9 | 0 |  | Exhaust grill | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | Present
56 | B |  | 1 | [6 empty] | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Good | 0.75 | 0 |  | 1x4 | [6 empty] | 0 |  |  | Other (describe) | 30+ |  | 30 | Good | 0.75 | 0 |  | Radiator | [6 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
1 | A | South West Corner | 3 | [6 empty] | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 |  |  | Brick painted | Reinforced Concrete | 30+ |  | 30 | Very Good | 0.9 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Exposed Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Exposed Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [11 empty] | N/A | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  | 1x4 | Toggle Wall Switches | 41136 |  | 11.5 | Fair | 0.5 |  |  | N/A | [8 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | smoke/strobe | [8 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A
53 | B |  | 3 | [6 empty] | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 |  |  | Brick painted | Reinforced Concrete | 30+ |  | 30 | Very Good | 0.9 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  | Painted | Exposed Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Exposed Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [11 empty] | N/A | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  | 1x4 | [8 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | smoke/strobe | [8 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A
54 | C |  | 1 | [6 empty] | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 |  |  | Brick painted | Reinforced Concrete | 30+ |  | 30 | Very Good | 0.9 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Exposed Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Exposed Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [11 empty] | N/A | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  | 1x4 | [8 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A | [7 empty] | Present | smoke/strobe | [8 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A
55 | D |  | 1 | Not fire stairs | [5 empty] | Other (describe) | 60+ |  | 60 | Very Poor | 0.1 |  |  | Brick painted | Steel Pan | 30+ |  | 30 | Very Good | 0.9 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Other (describe) | 30+ |  | 30 | Very Good | 0.9 |  |  | Painted | Other (describe) | 22 | 30 | 26 | Fair | 0.5 |  |  | Painted | [8 empty] | N/A | [8 empty] | N/A | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Good | 0.75 |  |  | 1x4 | [8 empty] | N/A | [17 empty] | N/A | [7 empty] | Present | smoke/strobe | [8 empty] | N/A | [8 empty] | N/A | [8 empty] | N/A
Pools | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Showers | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Swimming Pools
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
1 | A |  | Basement | [57 empty] | 0 | [80 empty] | 0 | [53 empty] | 0
Elevators | [9 empty] | Elevator | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Car Load Capacity | [8 empty] | Elevator Equipment and Controls
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
1 | A | Main Entrance | N/A | All Levels covered | [11 empty] | 0 | [17 empty] | 0 | [17 empty] | 0 | Present

## Master File (Systems)
Systems | Question | Value1 |  | Average1 | Systems | Question | Value1 | Average1 | Value2 | Average2 | Value3 | Average3
Systems | Seg ID | 506 |  |  | InfoTech | Seg ID | 183 |  | 5 |  | 4
| Bldg.Phase | A |  |  |  | Bldg.Phase | A |  | C |  | B
| Original | 1 |  |  |  | Original | 1 |  |  |  | 0
| Addition | 0 |  |  |  | Addition | 0 |  |  |  | 1
| Year Built | 1958 |  |  |  | Year Built | 1958 |  |  |  | 1976
Domestic Water Heaters | Location | UN/09 |  |  | Entrance Facilities (Demarc or Cable Vault) | Location |  |  | Adjacent to MDF Room
| Description | Fuel/Fired Water Heater |  |  |  | Description |  |  | Adjacent Demarc
| Age | 0 | 7 | 3.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition |  |  | Poor | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | 365,000 BTU |  |  |  | Notes
Sanitary Drainage | Location | Typical |  |  | Main Dist. Facility (MDF) | Location | Above Ground Level Floor |  | Above Ground Level Floor
| Description | Other (describe) |  |  |  | Description | Cabinet w/racks |  | MDF AGL
| Age | 60+ |  | 60 |  | Age | 41004 | 4.5
| Condition | Poor |  | 0.25 |  | Condition | Good | 0.75 | Good | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power |  |  | 220
| Notes | Cast Iron/Storm Drainage |  |  |  | Notes | Very secure and air conditioned; 0/5 years; 214A |  | Test C MDF
Building Support (other) Plumbing Systems | Location | Typical |  |  | MDF, HVAC Terminal Units | Location
| Description | Other (describe) |  |  |  | Description
| Age | 46 | 60 | 53 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Water Meter |  |  |  | Notes | Unknown
Fuel Piping | Location | UN/09 |  |  | MDF, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  |  | Description
| Age | 60+ |  | 60 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Steel |  |  |  | Notes | Unknown
Fuel Pumps | Location |  |  |  | Inter. Data Facility (IDF #1) | Location | 206
| Description |  |  |  |  | Description | Wall mtd.
| Age |  |  |  |  | Age | 41004 | 4.5
| Condition |  |  |  |  | Condition | Good | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes | Very secure and air conditioned; 0/5 years; 206
Fuel Storage Tanks | Location |  |  |  | IDF #1, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes | Unknown
Fuel Fired Boilers | Location | UN/09 |  |  | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers |  |  |  | Description
| Age | 60+ |  | 60 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Steam/4.2 million BTU/Condensate return tank/60+/Poor |  |  |  | Notes | Unknown
Furnaces | Location |  |  |  | Inter. Data Facility (IDF #2) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Unit Ventilators | Location |  |  |  | IDF #2, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Fan Coil Units | Location |  |  |  | IDF #2, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Water Chillers | Location |  |  |  | Inter. Data Facility (IDF #3) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Cooling Towers | Location |  |  |  | IDF #3, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Packaged Terminal Air Conditioner | Location |  |  |  | IDF #3, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Hydronic Piping System | Location |  |  |  | Inter. Data Facility (IDF #4) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Pumps | Location | UN/09 |  |  | IDF #4, HVAC Terminal Units | Location
| Description | Other (describe) |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Sump Pump |  |  |  | Notes
Steam Piping System | Location | Typical |  |  | IDF #4, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  |  | Description
| Age | 60+ |  | 60 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Steel |  |  |  | Notes
HVAC Air Distribution | Location |  |  |  | Inter. Data Facility (IDF #5) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Air Handling Units | Location | UN/10 |  |  | IDF #5, HVAC Terminal Units | Location
| Description | Indoor Air Handling Units (AHU) |  |  |  | Description
| Age | 40+ |  | 40 |  | Age
| Condition | Very Poor |  | 0.1 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 1 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Fans | Location | Roof |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  |  | Description
| Age | 40+ |  | 40 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Exhaust |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location |  |  |  | Backbone Cable Dist. | Location | Basement Closet
| Description |  |  |  |  | Description | Single Mode Fiber Cable
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition | Good | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Fire/Suppression (Standpipes), Water/Based | Location |  |  |  | Horizontal Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | N/A |  |  |  | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | UN/09
| Description | Gas Engine Generators
| Age | 46 | 60 | 53
| Condition | Very Poor |  | 0.1
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Not functional
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | N/A
Electrical Service & Distribution | Location | UN/16
| Description | D5010 120
| Age | 60+ |  | 60
| Condition | Poor |  | 0.25
CheckBox
Quantity
| Voltage | 120/208
| Power Output | 270kW
Elec Power
Notes
Voice Communication Terminal Equipment | Location | Typical
Description
| Age | 21 | 30 | 25.5
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Clock/Speaker
Distributed AV Communication (Paging) Systems | Location | UN/58
| Description | Other (describe)
| Age | 21 | 30 | 25.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Unknown Type
Video Surveillance Systems | Location | UN/58
| Description | Digital Video Recorders
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | UN/16
| Description | Fire/Smoke Detection Sensors
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | N/A
Other Equipment | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Value2 |  | Average2 | Exterior | Question | Value1 | Average1
Exterior | Seg ID | 375 |  |  | 398 |  |  | SiteElements | Seg ID | 139
| Bldg.Phase | A |  |  | B |  |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  |  | Addition | 0
| Year Built | 1958 |  |  | 1976 |  |  |  | Year Built | 1958
(Foundation) Walls for Subgrade Enclosures, Primary | Location | Typical |  |  | Typical |  |  | Roadways | Location
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place |  |  |  | Description
| Age | 60+ |  | 60 | 60+ |  | 60 |  | Age
| Condition | Good |  | 0.75 | Fair |  | 0.5 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location | Typical | [5 empty] | Parking Lots | Location | Typical
| Description | Brick, Solid (Mass) | [6 empty] | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 |  |  |  |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 |  |  |  |  | Condition | Poor | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Standard Slabs On Grade, Primary | Location | [6 empty] | Pedestrian Plazas and Walkways, Primary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Standard Slabs On Grade, Secondary | Location | [6 empty] | Pedestrian Plazas and Walkways, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Floor Construction, Primary | Location | Typical |  |  | Typical |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location
| Description | Wood, Beams and Joists |  |  | Steel Framing, w/ Steel Deck |  |  |  | Description
| Age | 60+ |  | 60 | 60+ |  | 60 |  | Age
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Floor Construction, Secondary | Location | [6 empty] | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Roof Construction, Structural Frame, Primary | Location | Typical |  |  | Typical |  |  | Site Lighting, Primary | Location | Typical
| Description | Wood, Beams and Joists |  |  | Steel Framing, w/ Steel Deck |  |  |  | Description | Pole Mounted H.I.D.
| Age | 60+ |  | 60 | 60+ |  | 60 |  | Age | 41136 | 11.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Very Good | 0.9
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Roof Construction, Structural Frame, Secondary | Location | [6 empty] | Site Lighting, Secondary | Location | Typical
| Description | [7 empty] | Description | Pole Mounted H.I.D.
| Age | [7 empty] | Age | 30+ | 30
| Condition | [7 empty] | Condition | Very Poor | 0.1
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | Pole mounted not in operation
Exterior Walls / Exterior Assembly, Primary | Location | Typical |  |  | Typical |  |  | Playground Surface | Location | Typical
| Description | Brick, Solid (Mass) |  |  | Brick, Solid (Mass) |  |  |  | Description | Other (describe)
| Age | 60+ |  | 60 | 60+ |  | 60 |  | Age | 41136 | 11.5
| Condition | Good |  | 0.75 | Good |  | 0.75 |  | Condition | Very Good | 0.9
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | Synthetic Soft Surface
Exterior Walls / Exterior Assembly, Secondary | Location | Entry |  |  | Typical |  |  | Playground Equipment | Location | Typical
| Description | Other (describe) |  |  | Stone Veneer w/ CMU B/U |  |  |  | Description | Multi/Component Play Equipment Set
| Age | 60+ |  | 60 | 60+ |  | 60 |  | Age | 41136 | 11.5
| Condition | Good |  | 0.75 | Good |  | 0.75 |  | Condition | Good | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Stone with tile / entrance only | [6 empty] | Notes
Exterior Windows, Primary | Location | Typical |  |  | Typical |  |  | TCUs | Location
| Description | Aluminum, Casement |  |  | Aluminum, Casement |  |  |  | Description
| Age | 16 | 21 | 18.5 | 16 | 21 | 18.5 |  | Age
| Condition | Very Good |  | 0.9 | Very Good |  | 0.9 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated) |  |  | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Security Grilles |  |  | Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location | Typical |  |  | Typical
| Description | Steel (Hollow) |  |  | Steel (Hollow)
| Age | 60+ |  | 60 | 16 | 30 | 23
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location | Typical
| Description | Wood
| Age | 60+ |  | 60
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Solid
Roofing, Primary | Location | Typical |  |  | Typical
| Description | Asphalt Shingle |  |  | Polyurethane, Spray Applied
| Age | 41136 |  | 11.5 | 41136 |  | 11.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Secondary | Location |  |  |  | Typical
| Description |  |  |  | Metal, Seam
| Age |  |  |  | 41136 |  | 11.5
| Condition |  |  |  | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | Bulkhead wall finish
Roof (Accessories) Supplementary Components / Flashing and Trim | Location | Typical |  |  | Typical
| Description | Aluminum |  |  | Metal, Galvanized/Painted
| Age | 41136 |  | 11.5 | 41136 |  | 11.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Corrugated metal siding parapet / 30yr/1 |  |  | Also copper fascia detail at areas
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location | Typical |  |  | Typical
| Description | Metal, Galvanized/Painted |  |  | Other (describe)
| Age | 30+ |  | 30 | 41136 |  | 11.5
| Condition | Fair |  | 0.5 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | Internal drains
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes