## FCI Summary
Building Name: | Quitman Street | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 122313
Number of Floors: | B + 3
School Age (years): | 51
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 24.76%
Facility Condition = | FAIR
FCI Deficiency Cost = | 6246793.0268
FCI Replacement Cost = | 25227056.25
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 541
Historic 2005 LRFP Capacity = | 538
Adjusted 2012 Capacity = | 774
Recent Occupancy % = | 69.9%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 98.7%
Classroom Adequacy = | VERY GOOD
Special Spaces Adequacy % Score = | 81.13%
Special Spaces Adequacy = | FAIR

## Uniformat FCI
Building Name: |  | Quitman Street | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 122313
Largest Floor Level Area: |  | 49309
Vertical FAR Ratio: |  | 2.4805
School Age (years): |  | 51
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 2.7% | 5.5687 | 122313 | 681130.5187 | 100 | 51 | 49 | 0.5 | 50 | 99 | 674319.2136 | 6811.3052 | 1%
|  |  | A1030 - SLAB ON GRADE | 2.65% | 5.4656 | 122313 | 668516.9906 | 100 | 51 | 49 | 0.5 | 50 | 99 | 661831.8207 | 6685.1699 | 1%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 122313 | 554995.2375 | 100 | 51 | 49 | 0.75 | 75 | 100 | 554995.2375 | 0 | 0%
|  |  | SUBTOTAL SUBSTRUCTURE | 7.55% | 15.5719 | 122313 | 1904642.7469
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 122313 | 2774976.1875 | 100 | 51 | 49 | 0.5 | 50 | 99 | 2747226.4256 | 27749.7619 | 1%
|  |  | B1020 - ROOF CONSTRUCTION | 3.4% | 7.0125 | 122313 | 857719.9125 | 100 | 51 | 49 | 0.5 | 50 | 99 | 849142.7134 | 8577.1991 | 1%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 7.7% | 15.8812 | 122313 | 1942483.3313 | 100 | 51 | 49 | 0.5 | 50 | 99 | 1923058.4979 | 19424.8333 | 1%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 4.4% | 9.075 | 122313 | 1109990.475 | 30 | 9.5 | 20.5 | 0.75 | 22.5 | 30 | 1109990.475 | 0 | 0%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 3% | 6.1875 | 122313 | 756811.6875 | 30 | 11.5 | 18.5 | 0.75 | 22.5 | 30 | 756811.6875 | 0 | 0%
|  |  | SUBTOTAL SHELL | 29.5% | 60.8438 | 122313 | 7441981.5938
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 122313 | 1009082.25 | 60 | 50.4545 | 9.5455 | 0.52273 | 31.3636 | 40.9091 | 688010.625 | 321071.625 | 31.82%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 122313 | 378405.8438 | 20 | 22.6061 | 0 | 0.3 | 5 | 5 | 94601.4609 | 283804.3828 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 122313 | 1009082.25 | 20 | 7.5 | 12.5 | 0.65 | 13 | 20 | 1009082.25 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 122313 | 378405.8438 | 30 | 51 | 0 | 0.5 | 5 | 5 | 63067.6406 | 315338.2031 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 3.2% | 6.6 | 122313 | 807265.8 | 10 | 11.1765 | 0 | 0.5 | 5 | 5 | 403632.9 | 403632.9 | 50%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 122313 | 1513623.375 | 20 | 19.6471 | 0.35294 | 0.33529 | 6.7059 | 7.0588 | 534220.0147 | 979403.3603 | 64.71%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 122313 | 1513623.375 | 30 | 29.0625 | 0.9375 | 0.38438 | 11.5312 | 12.4688 | 629099.7152 | 884523.6598 | 58.44%
|  |  | SUBTOTAL INTERIORS | 26.2% | 54.0375 | 122313 | 6609488.7375
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 0.7% | 1.4438 | 122313 | 176589.3938 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 176589.3938 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 122313 | 378405.8438 | 60 | 29.0934 | 30.9066 | 0.455 | 27.3 | 58.2066 | 367095.1603 | 11310.6834 | 2.989%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 122313 | 327951.7313 | 60 | 3.5 | 56.5 | 0.9 | 54 | 60 | 327951.7313 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 122313 | 302724.675 | 60 | 51 | 9 | 0.25 | 15 | 24 | 121089.87 | 181634.805 | 60%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 122313 | 126135.2812 | 30 | 7.5 | 22.5 | 0.75 | 22.5 | 30 | 126135.2812 | 0 | 0%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 3.2% | 6.6 | 122313 | 807265.8 | 60 | 51 | 9 | 0.25 | 15 | 24 | 322906.32 | 484359.48 | 60%
|  |  | D3020 - BOILERS | 2.5% | 5.1562 | 122313 | 630676.4062 | 60 | 7.5 | 52.5 | 0.7 | 42 | 60 | 630676.4062 | 0 | 0%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4.5% | 9.2812 | 122313 | 1135217.5312 | 40 | 46.5 | 0 | 0.5625 | 5 | 5 | 141902.1914 | 993315.3398 | 87.5%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4.5% | 9.2812 | 122313 | 1135217.5312 | 40 | 32.9885 | 7.0115 | 0.36954 | 14.7816 | 21.7931 | 618497.8274 | 516719.7039 | 45.52%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 0% | 0 | 122313 | 0 | 40 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0%
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.5% | 3.0938 | 122313 | 378405.8438 | 20 | 7.5 | 12.5 | 0.75 | 15 | 20 | 378405.8438 | 0 | 0%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 122313 | 252270.5625 | 20 | 7.5 | 12.5 | 0.75 | 15 | 20 | 252270.5625 | 0 | 0%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 122313 | 50454.1125 | 20 | 16.75 | 3.25 | 0.625 | 12.5 | 15.75 | 39732.6136 | 10721.4989 | 21.25%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 122313 | 327951.7313 | 60 | 51 | 9 | 0.25 | 15 | 24 | 131180.6925 | 196771.0388 | 60%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 122313 | 1765893.9375 | 30 | 12.8966 | 17.1034 | 0.57241 | 17.1724 | 30 | 1765893.9375 | 0 | 0%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 122313 | 756811.6875 | 20 | 4.763 | 15.237 | 0.79505 | 15.901 | 20 | 756811.6875 | 0 | 0%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 122313 | 75681.1687 | 20 | 41.5 | 0 | 0.29074 | 5 | 5 | 18920.2922 | 56760.8766 | 75%
|  |  | SUBTOTAL SERVICES | 34.2% | 70.5375 | 122313 | 8627653.2375
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 122313
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 122313
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 122313
|  |  | E1090 - OTHER EQUIPMENT |  |  | 122313
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 122313
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 122313
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 122313
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 122313
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 122313
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 122313 | 252270.5625 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 63067.6406 | 189202.9219 | 75%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 122313 | 126135.2812 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 31533.8203 | 94601.4609 | 75%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 122313 | 126135.2812 | 30 | 30 | 0 | 0.5 | 15 | 15 | 63067.6406 | 63067.6406 | 50%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 122313 | 126135.2812 | 30 | 18.5 | 11.5 | 0.5 | 15 | 26.5 | 111419.4984 | 14715.7828 | 11.67%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 122313 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 122313
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 122313 | 25227056.25 | [7 empty] | 6246793.0268 | 24.76%
99.95%

## Master File (Interior)
Quitman Street
School Code: | 605
NPS Code: | 89
Street: | 21 Quitman St.
City/Town: | Newark, NJ 07103
Database ID: | 15
Total size (gsf): | 122269
ROOM INFORMATION | [11 empty] | Average Age | 50 | Ave Condition | 0.5 | [5 empty] | Average Age | 19.6471 | Ave Condition | 0.33529 | [5 empty] | Average Age | 11.1765 | Ave Condition | 0.5 | [5 empty] | Average Age | 29.0625 | Ave Condition | 0.38438 | [5 empty] | Average Age | 22.6061 | Ave Condition | 0.3 | [5 empty] | Average Age | 50.4545 | Ave Condition | 0.52273 | [5 empty] | Average Age | 28.3421 | Ave Condition | 0.5 | [5 empty] | Average Age | 30 | Ave Condition | 0.4375 | [5 empty] | Average Age | 30 | Ave Condition | 0.4375 | [5 empty] | Average Age | 30 | Ave Condition | 0.5 | [5 empty] | Average Age | 27.125 | Ave Condition | 0.4 | [5 empty] | Average Age | 7.5 | Ave Condition | 0.65 | [5 empty] | Average Age | 14.2931 | Ave Condition | 0.64483 | [5 empty] | Average Age | 30 | Ave Condition | 0.48148 | [5 empty] | Average Age | 28.9655 | Ave Condition | 0.40862 | [5 empty] | Average Age | 30 | Ave Condition | 0.2 | [5 empty] | Average Age | 16.75 | Ave Condition | 0.625 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 4.6042 | Ave Condition | 0.51042 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [8 empty] | Plumbing Fixtures - Urinals | [8 empty] | Plumbing Fixtures - Showers | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
1575 | UN-1 | Custodial & General Storage | Basement | A | Support |  |  | 314 | 10' 0" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1576 | UN-2 | Men\'s Custodal Locker Room | Basement | A | Support |  |  | 128 | 8' 0" | [9 empty] | Other (describe) | 20+ |  | 20 | Poor | 0.25 | 0 |  | Unfinished Concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Recessed Fixture | 30+ |  | 30 | Very Poor | 0.1 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Exhaust Grill | [24 empty] | 0 | Present | [133 empty] | 0 | Present
1577 | UN-3 | Water Closet | Basement | A | Support |  |  | 82 | 8' 0" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  | Ceramic Tile Wainscot | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Good | 0.75 | 1 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Poor | 0.25 | 1 |  |  | Wall Hung | 30+ |  | 30 | Fair | 0.5 | 1 | [17 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 2' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Exhaust Grill | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0 | Present
1578 | UN-4 | Womens Custodial Locker Room | Basement | A | Support |  |  | 178 | 8' 0" | [9 empty] | Unfinished | [17 empty] | Plaster
1579 | UN-5 | Water Closet | Basement | A | Support |  |  | 92 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1580 | UN-6 | Equipment Storage | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 147 | N/A
1581 | UN-7 | Meter Room | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 81 | N/A
1582 | UN-8 | Equipment Storage | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 43 | N/A
1583 | UN-9 | Boys\' Water Closet | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 255 | 8' 0" | Plaster Partitions/on CMU Back-up Wall | 46 | 60 | 53 | Poor | 0.25 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  | Ceramic Tile Wainscot | Plaster | 30+ |  | 30 | Very Poor | 0.1 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Poor | 0.25 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 4 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 2 |  |  | Floor Trough | 30+ |  | 30 | Poor | 0.25 | 3 | [8 empty] | 0 | [8 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Recessed Fixture | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | 1' x 4' | [6 empty] | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
1584 | UN-10 | Custodial Closet | Basement | A | Support |  |  | 16 | 10' 0" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1585 | UN-11 | Male Instructor | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 191 | N/A
1586 | UN-12 | Water Closet | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 28 | N/A
1587 | UN-13 | Interior Playcourt | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 6031 | 13' 3" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [38 empty] | Wall Mounted China Drinking Fountains | 30+ |  | 30 | Very Poor | 0.1 | 0 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  | 1' x 4' - Several Broken, Need Protective Grill | [9 empty] | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | 0 |  | Exhaust Grill | [9 empty] | Wet Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | Present | [133 empty] | 0 | Present | Poor Condition
1588 | UN-14 | Girls' Water Closet | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 289 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 5 | [8 empty] | 4 | [8 empty] | 0
1589 | UN-15 | Female Instructor | Basement | A | Phys. Ed. (Gym + Storage) |  |  | 250 | N/A
1590 | UN-16 | Electric Room | Basement | A | Support |  |  | 152 | N/A
1591 | UN-17 | Boiler Room | Basement | A | Support |  |  | 1791 | N/A
1592 | UN-18 | Electrical Room | Basement | A | Support |  |  | 31 | N/A
1593 | 100 | Home Economics | 1st Floor | A | Technological Literacy |  |  | 1076 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1594 | 101 | Parent Room | 1st Floor | A | Administration |  |  | 943 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1595 | 102 | Classroom | 1st Floor | A | General Classroom |  |  | 901 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1596 | 107 | Office | 1st Floor | A | Administration |  |  | 885 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1597 | 108 | Classroom | 1st Floor | A | General Classroom |  |  | 886 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1598 | 109 | Classroom | 1st Floor | A | General Classroom |  |  | 917 | 9' 7" | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [62 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
1599 | 110 | 1st Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 819 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1600 | 111 | 2nd Grade Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 860 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  | Drinking Fountain Attached | [45 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [26 empty] | 3 | [71 empty] | 0 | Present
1601 | 112 | Classroom | 1st Floor | A | General Classroom |  |  | 834 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1602 | 115 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 1062 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1603 | 116 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 1060 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1604 | 117 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 1209 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  | Drinking Fountain Attached | [27 empty] | Other (describe) | 30+ |  | 30 | Good | 0.75 | 0 |  | In-Counter Attached to Lavatory | [9 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [35 empty] | 2 | [71 empty] | 0 | Present
1605 | 118 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 1045 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1606 | 119 | Office | 1st Floor | A | Administration |  |  | 899 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  | Damaged Perimeter Exterior Wall Cabinet | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1607 | 120 | Classroom | 1st Floor | A | General Classroom |  |  | 919 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1608 | 121 | Teachers\' Resource Room | 1st Floor | A | Administration |  |  | 907 | 9' 7 | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0 | Present
1609 | UN-19 | Waiting Room (Jewish Renaissance Medical Center) | 1st Floor | A | Health Services |  |  | 129 | 7' 10 | [9 empty] | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Fair | 0.5 |  |  | 2' x 4' | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Plaster/Metal Stud Framing | 31 | 45 | 38 | Good | 0.75 | [57 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  | 2' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 41136 |  | 11.5 | Good | 0.75 |  |  | HVAC Diffuser | [25 empty] | Present | [35 empty] | Present | [98 empty] | Present | Paging Phone
1610 | UN-20 | Nurse Office (Jewish Renaissance Medical Center) | 1st Floor | A | Health Services |  |  | 218 | 7' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1611 | UN-21 | Utility Room (Jewish Renaissance Medical Center) | 1st Floor | A | Health Services |  |  | 32 | 7' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1612 | UN-22 | Exam Room (Jewish Renaissance Medical Center) | 1st Floor | A | Health Services |  |  | 119 | 7' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1613 | UN-23 | Exam Room (Jewish Renaissance Medical Center) | 1st Floor | A | Health Services |  |  | 108 | 7' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1614 | UN-24 | Office (Jewish Renaissance Medical Center) | 1st Floor | A | Health Services |  |  | 105 | 7' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1615 | UN-25 | Office (Jewish Renaissance Medical Center) | 1st Floor | A | Health Services |  |  | 101 | 7' 10 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1616 | UN-26 | School Health Office | 1st Floor | A | Health Services |  |  | 376 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1617 | UN-27 | Waiting Room | 1st Floor | A | Health Services |  |  | 242 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Return Ventilation Wall-Grill | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0
1618 | UN-28 | Conference Room | 1st Floor | A | Health Services |  |  | 188 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1619 | UN-29 | Water Closet | 1st Floor | A | Health Services |  |  | 50 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1620 | UN-30 | Main Office | 1st Floor | A | Administration |  |  | 777 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Carpet | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1621 | UN-31 | Principals Conference Room | 1st Floor | A | Administration |  |  | 156 | 9' 7" | CMU Back-up Wall | 16 | 30 | 23 | Poor | 0.25 | 0 |  |  | Carpet | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Window Mounted | 30+ |  | 30 | Very Poor | 0.1 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1622 | UN-32 | Principals Office | 1st Floor | A | Administration |  |  | 204 | 9' 7" | [9 empty] | Carpet | [17 empty] | Acoustical Panel
1623 | UN-33 | Water Closet | 1st Floor | A | Administration |  |  | 46 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1624 | UN-34 | Safe | 1st Floor | A | Administration |  |  | 85 | N/A
1625 | UN-35 | Storage | 1st Floor | A | Administration |  |  | 94 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1626 | UN-36 | Back Stage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 198 | 15 '9" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1627 | UN-37 | Stage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 586 | 12' 3" | [9 empty] | Wood | [17 empty] | Plaster
1628 | UN-38 | Cafetorium | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 5239 | 15' 0" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  | Sky Light Wells (Boarded Up) - 50yrs / Very Poor Condition | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [56 empty] | Fluorescent Lay-In Fixture (Troffer) | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  | 2' x 4' | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | HVAC Ceiling Diffusers; Exhaust Grills - 50yrs / Poor Condition | [6 empty] | 0 |  |  | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 | 0 | [9 empty] | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [108 empty] | Present | Auditorium Speaker System - 50 yrs / Fair Condition
1629 | UN-39 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 64 | N/A
1630 | UN-40 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 97 | N/A
1631 | UN-41 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 131 | 10' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Unfinished Ceiling
1632 | UN-42 | Kitchen | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 1348 | 15' 0" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  | Damaged Area at Corner | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Metal/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Stainless Steel Sinks | 16 | 21 | 18.5 | Good | 0.75 | [48 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 16 | 21 | 18.5 | Good | 0.75 | 0 |  | Kitchen Exhaust Hood | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Gas-Fired Unit Heater | Dry Chemical | 16 | 21 | 18.5 | Good | 0.75 | 0 |  | Ansul Fire Suppression @ Kitchen Exhaust Hood | [6 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [107 empty] | 0 | Present | Paging Phone | [24 empty] | 0 | Present | [7 empty] | 0 | Present
1633 | UN-43 | Locker Room | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 45 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1634 | UN-44 | Water Closet | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 32 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1635 | UN-45 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 121 | 10' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1636 | UN-46 | Kitchen | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 674 | 10' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1637 | UN-47 | Office | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 47 | 7' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1638 | UN-48 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 198 | 10' 1" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1639 | UN-49 | Boys\' Locker Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 474 | 8' 0" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Other (describe) | 20+ |  | 20 | Poor | 0.25 | 0 |  | Painted Concrete | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 | [35 empty] | 0 |  |  | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 |  |  | Fluorescent Recessed Fixture | 30+ |  | 30 | Poor | 0.25 | 0 |  | 1' x 4' | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0
1640 | UN-50 | Drying Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 82 | N/A
1641 | UN-51 | Shower Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 107 | N/A
1642 | UN-52 | Water Closet | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 159 | 8' 0" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  | Ceramic Tile Wainscot | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 3 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Poor | 0.25 | 2 |  |  | Wall Hung | 30+ |  | 30 | Fair | 0.5 | 1 | [8 empty] | 0 | [8 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Recessed Fixture | 30+ |  | 30 | Poor | 0.25 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Wall Exhaust Grill | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0
1643 | UN-53 | Gymnasium | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 4890 | 18' 0" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Exposed Concrete Plank and Steel Structural Frame | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Demountable/Folding. | 46 | 60 | 53 | Poor | 0.25 | 0 | [56 empty] | Other (describe) | 41136 |  | 11.5 | Good | 0.75 | 0 |  | H.I.D. Pendant Mount Fixture (Metal Halide) | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 |  |  | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [107 empty] | 0 | Present | Broken Clock
1644 | UN-54 | Storage | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 206 | N/A
1645 | UN-55 | Female Instructor | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 161 | N/A
1646 | UN-56 | Male Instructor | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 191 | N/A
1647 | UN-57 | Storage | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 214 | N/A
1648 | UN-58 | Girls' Locker Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 468 | 8' 0" | [9 empty] | Unfinished | [17 empty] | Plaster
1649 | UN-59 | Drying Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 62 | N/A
1650 | UN-60 | Shower Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 91 | N/A
1651 | UN-61 | Water Closet | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 179 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 3 | [8 empty] | 3 | [8 empty] | 0
1652 | UN-62 | Boys' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 50 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1653 | UN-63 | Girls' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 50 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1654 | UN-64 | Storage | 1st Floor | A | Kindergarten Classroom |  |  | 69 | N/A
1655 | UN-65 | Boys' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 50 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1656 | UN-66 | Girls' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 50 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1657 | UN-67 | Storage | 1st Floor | A | Kindergarten Classroom |  |  | 69 | N/A
1658 | UN-68 | Faculty Room | 1st Floor | A | Faculty Support |  |  | 565 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Defibrillator | [15 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1659 | UN-69 | Powder Room | 1st Floor | A | Faculty Support |  |  | 68 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1660 | UN-70 | Women's Water Closet | 1st Floor | A | Faculty Support |  |  | 77 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1661 | UN-71 | Men's Water Closet | 1st Floor | A | Faculty Support |  |  | 77 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1662 | UN-72 | Book Room | 1st Floor | A | Support |  |  | 255 | N/A
1663 | UN-73 | Girls' Water Closet | 1st Floor | A | Support |  |  | 384 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 5 | [8 empty] | 9 | [8 empty] | 0
1664 | UN-74 | Custodial Closet | 1st Floor | A | Support |  |  | 19 | 9' 7" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1665 | UN-75 | Storage | 1st Floor | A | Support |  |  | 19 | 9' 7" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1666 | UN-76 | Boys\' Water Closet | 1st Floor | A | Support |  |  | 384 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  | Ceramic Tile Wainscot | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 5 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 5 |  |  | Floor Unit | 30+ |  | 30 | Poor | 0.25 | 9 | [20 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Very Poor | 0.1 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0
1667 | UN-77 | Storage | 1st Floor | A | Kindergarten Classroom |  |  | 85 | N/A
1668 | UN-78 | Girls' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 61 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1669 | UN-79 | Boys' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 60 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1670 | UN-80 | Storage | 1st Floor | A | Kindergarten Classroom |  |  | 86 | N/A
1671 | UN-81 | Girls' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 61 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1672 | UN-82 | Boys' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 60 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1673 | 200 | Library | 2nd Floor | A | Media Center |  |  | 1210 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Poor | 0.25 | 0 |  | Interior Fixed Window into UN-84 | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 0 | 3 | 1.5 | Good | 0.75 | 0 | [17 empty] | 1 |  | Portable - First Generation | [15 empty] | 8 | [71 empty] | 0 | Present
1674 | 201 | Classroom | 2nd Floor | A | General Classroom |  |  | 943 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1675 | 202 | Classroom | 2nd Floor | A | General Classroom |  |  | 901 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1676 | 203 | 2nd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 881 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1677 | 204 | Resource Room | 2nd Floor | A | Administration |  |  | 881 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [48 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1678 | 205 | Classroom | 2nd Floor | A | General Classroom |  |  | 885 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1679 | 206 | Classroom | 2nd Floor | A | General Classroom |  |  | 884 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1680 | 207 | Classroom | 2nd Floor | A | General Classroom |  |  | 885 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [35 empty] | 3 | [71 empty] | 0 | Present
1681 | 208 | Classroom | 2nd Floor | A | General Classroom |  |  | 886 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1682 | 209 | 1st Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 917 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1683 | 210 | Classroom | 2nd Floor | A | General Classroom |  |  | 836 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1684 | 211 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 860 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1685 | 212 | 4th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 851 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1686 | 213 | 5th Grade Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 788 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1687 | 214 | 6th Grade Classroom | 2nd Floor | A | General Classroom (Grades 6-8) |  |  | 852 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [35 empty] | 3 | [71 empty] | 0 | Present
1688 | 215 | 3rd Grade Classroom | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 852 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1689 | 216 | Art Room | 2nd Floor | A | Visual & Performing Arts |  |  | 911 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Demountable/Folding. | 46 | 60 | 53 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [107 empty] | 0 | Present
1690 | 217 | Art Room | 2nd Floor | A | Visual & Performing Arts |  |  | 909 | 9' 7 | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1691 | 218 | Classroom | 2nd Floor | A | General Classroom |  |  | 901 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1692 | 219 | Classroom | 2nd Floor | A | General Classroom |  |  | 899 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1693 | 220 | Teachers Resource | 2nd Floor | A | Administration |  |  | 919 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1694 | 221 | CST Office | 2nd Floor | A | Administration |  |  | 907 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1695 | UN-84 | Workroom | 2nd Floor | A | Media Center |  |  | 84 | N/A
1696 | UN-85 | Mechanical Equipment | 2nd Floor | A | Support |  |  | 2024 | N/A
1697 | UN-86 | Mechanical Equipment | 2nd Floor | A | Support |  |  | 417 | N/A
1698 | UN-87 | Faculty Room | 2nd Floor | A | Faculty Support |  |  | 565 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1699 | UN-88 | Powder Room | 2nd Floor | A | Faculty Support |  |  | 68 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1700 | UN-89 | Women's Water Closet | 2nd Floor | A | Faculty Support |  |  | 77 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1701 | UN-90 | Men's Water Closet | 2nd Floor | A | Faculty Support |  |  | 77 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1702 | UN-91 | Book Room | 2nd Floor | A | Support |  |  | 255 | N/A
1703 | UN-92 | Girls\' Water Closet | 2nd Floor | A | Support |  |  | 384 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  | Ceramic Tile Wainscot | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 5 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 9 | [8 empty] | 0 | [20 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Poor | 0.25 | 0 |  |  | Fluorescent Recessed Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4'; (3) 1' x 4' Fluorescent Surface Mount Fixture - 10yrs / Good Condition | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0
1704 | UN-93 | Custodial Closet | 2nd Floor | A | Support |  |  | 19 | 9' 7" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1705 | UN-94 | Storage | 2nd Floor | A | Support |  |  | 19 | 9' 7" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1706 | UN-95 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 384 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 5 | [8 empty] | 5 | [8 empty] | 9
1707 | 300 | Renaissance Office | 3rd Floor | A | Administration |  |  | 1055 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1708 | 301 | 4th Grade Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 943 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1709 | 302 | Classroom | 3rd Floor | A | General Classroom |  |  | 901 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1710 | 303 | Classroom | 3rd Floor | A | General Classroom |  |  | 881 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [26 empty] | 3 | [71 empty] | 0 | Present
1711 | 304 | Classroom | 3rd Floor | A | General Classroom |  |  | 884 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1712 | 305 | Lead Science Teacher | 3rd Floor | A | Science (6-12) |  |  | 885 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present
1713 | 306 | Classroom | 3rd Floor | A | General Classroom |  |  | 884 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1714 | 307 | Classroom | 3rd Floor | A | General Classroom |  |  | 885 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1715 | 308 | Classroom | 3rd Floor | A | General Classroom |  |  | 886 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1716 | 309 | Classroom | 3rd Floor | A | General Classroom |  |  | 917 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1717 | 310 | Computer Lab | 3rd Floor | A | Technological Literacy |  |  | 836 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1718 | 311 | 7th Grade Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 860 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1719 | 312 | Classroom | 3rd Floor | A | General Classroom |  |  | 851 | 9' 7" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Good | 0.75 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [47 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [9 empty] | Present | [16 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [35 empty] | 2 | [72 empty] | Present
1720 | 313 | Classroom | 3rd Floor | A | General Classroom |  |  | 800 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1721 | 314 | Social Worker | 3rd Floor | A | Administration |  |  | 864 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1722 | 315 | Classroom | 3rd Floor | A | General Classroom |  |  | 865 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1723 | 316 | Special Education Classroom | 3rd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 901 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1724 | 317 | Classroom | 3rd Floor | A | General Classroom |  |  | 900 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1725 | 318 | Classroom | 3rd Floor | A | General Classroom |  |  | 901 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1726 | 319 | Classroom | 3rd Floor | A | General Classroom |  |  | 899 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1727 | 320 | Music | 3rd Floor | A | Visual & Performing Arts |  |  | 919 | 9' 7 | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Very Poor | 0.1 | 0 |  | Concealed Spline | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 | [35 empty] | 0 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  | 1' x 4' | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 41004 |  | 4.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0 | Present
1728 | 321 | Classroom | 3rd Floor | A | General Classroom |  |  | 907 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1729 | UN-96 | Storage | 3rd Floor | A | Administration |  |  | 88 | N/A
1730 | UN-97 | Storage | 3rd Floor | A | Administration |  |  | 138 | N/A
1731 | UN-98 | Faculty Room | 3rd Floor | A | Faculty Support |  |  | 565 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
1732 | UN-99 | Powder Room | 3rd Floor | A | Faculty Support |  |  | 68 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
1733 | UN-100 | Women's Water Closet | 3rd Floor | A | Faculty Support |  |  | 77 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1734 | UN-101 | Men's Water Closet | 3rd Floor | A | Faculty Support |  |  | 77 | 8' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
1735 | UN-102 | Book Room | 3rd Floor | A | Support |  |  | 255 | N/A
1736 | UN-103 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 384 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 5 | [8 empty] | 9 | [8 empty] | 0
1737 | UN-104 | Custodial Closet | 3rd Floor | A | Support |  |  | 19 | 9' 7" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1738 | UN-105 | Storage | 3rd Floor | A | Support |  |  | 19 | 9' 7" | [9 empty] | Unfinished | [17 empty] | Unfinished Ceiling
1739 | UN-106 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 384 | 9' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [32 empty] | 5 | [8 empty] | 5 | [8 empty] | 9
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
6 | A | @ Quitman Street Entrance | 1st | [6 empty] | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Very Good | 0.9 | [12 empty] | Concrete Block | 46 | 60 | 53 | Good | 0.75 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ |  | 30 | Fair | 0.5 |  |  | 2' x 2' | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Terminal Unit Heaters | 30+ |  | 30 | Fair | 0.5 | [19 empty] | Present | [17 empty] | Present
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
16 | A | @ UN-53 (Gymnasium) | 1st | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Very Poor | 0.1 | [12 empty] | Concrete Block | 46 | 60 | 53 | Good | 0.75 |  |  |  | Wall Mounted Stainless Steel Drinking Fountains | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ |  | 30 | Fair | 0.5 |  |  | 1' x 4' | [18 empty] | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 | [10 empty] | Present | [17 empty] | Present
17 | B | @ Entry Lobby #1 | 1st | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Very Good | 0.9 | [12 empty] | Concrete Block | 46 | 60 | 53 | Good | 0.75 | [21 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ |  | 30 | Fair | 0.5 |  |  | 1' x 4' | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present | [17 empty] | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
12 | A | @ 112 (Classroom) | 1st | [6 empty] | Other (describe) | 46 | 60 | 53 | Fair | 0.5 |  |  | Curtain Wall Assembly | Steel Pan | 30+ |  | 30 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Terrazzo | 30+ |  | 30 | Poor | 0.25 |  |  |  | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [12 empty] | Fluorescent Recessed Fixture | 30+ |  | 30 | Fair | 0.5 |  |  | 1' x 4' | [34 empty] | Present | [17 empty] | Present
13 | B | @ Entry Lobby #1 | 1st | [6 empty] | Brick, Exposed/Unfinished | 46 | 60 | 53 | Fair | 0.5 |  |  | Curtain Wall Assembly at Sides | Steel Pan | 30+ |  | 30 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [12 empty] | Fluorescent Recessed Fixture | 30+ |  | 30 | Fair | 0.5 |  |  | 1' x 4' | [34 empty] | Present | [17 empty] | Present

## Master File (Systems)
Systems | Question | Value1 |  | Average1 | Systems | Question | Value1 | Average1
Systems | Seg ID | 982 |  |  | InfoTech | Seg ID | 55
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 0 |  |  |  | Addition | 0
| Year Built |  |  |  |  | Year Built
Domestic Water Heaters | Location | UN/17 |  |  | Entrance Facilities (Demarc or Cable Vault) | Location
| Description | Fuel/Fired Water Heater |  |  |  | Description
| Age | 0 | 7 | 3.5 |  | Age
| Condition | Very Good |  | 0.9 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Gas/Fired / 344 MBH |  |  |  | Notes
Sanitary Drainage | Location | UN/18 |  |  | Main Dist. Facility (MDF) | Location | Ground Level Floor
| Description | Sanitary Sewers |  |  |  | Description | Cabinet
| Age | 46 | 60 | 53 |  | Age | 41004 | 4.5
| Condition | Poor |  | 0.25 |  | Condition | Very Good | 0.9
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Cast/Iron |  |  |  | Notes | at Room UN/72
Building Support (other) Plumbing Systems | Location | UN/17 |  |  | MDF, HVAC Terminal Units | Location
| Description | Stormwater Area Drains |  |  |  | Description
| Age | 0 | 15 | 7.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Copper Piping |  |  |  | Notes
Fuel Piping | Location | UN/17 |  |  | MDF, Packaged Terminal Air Conditioner | Location
| Description | Gas Piping |  |  |  | Description
| Age | 0 | 15 | 7.5 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Steel |  |  |  | Notes
Fuel Pumps | Location |  |  |  | Inter. Data Facility (IDF #1) | Location | UN/91
| Description |  |  |  |  | Description | Cabinet
| Age |  |  |  |  | Age | 41004 | 4.5
| Condition |  |  |  |  | Condition | Very Good | 0.9
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Storage Tanks | Location |  |  |  | IDF #1, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Fired Boilers | Location | UN/17 |  |  | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers |  |  |  | Description
| Age | 0 | 15 | 7.5 |  | Age
| Condition | Very Good |  | 0.9 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | 6 Boilers |  |  |  | Notes
Furnaces | Location |  |  |  | Inter. Data Facility (IDF #2) | Location | UN/102
| Description |  |  |  |  | Description | Cabinet
| Age |  |  |  |  | Age | 41004 | 4.5
| Condition |  |  |  |  | Condition | Very Good | 0.9
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Unit Ventilators | Location | Typical |  |  | IDF #2, HVAC Terminal Units | Location
| Description | Vertical HV (w/heating only) |  |  |  | Description
| Age | 40+ |  | 40 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fan Coil Units | Location |  |  |  | IDF #2, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Water Chillers | Location |  |  |  | Inter. Data Facility (IDF #3) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Cooling Towers | Location |  |  |  | IDF #3, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Packaged Terminal Air Conditioner | Location |  |  |  | IDF #3, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Hydronic Piping System | Location | UN/17 |  |  | Inter. Data Facility (IDF #4) | Location
| Description | Zoned Hot Water System |  |  |  | Description
| Age | 46 | 60 | 53 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | New Pumping; Boiler / 3 yrs / Good Condition |  |  |  | Notes
Pumps | Location | UN/17 |  |  | IDF #4, HVAC Terminal Units | Location
| Description | Other (describe) |  |  |  | Description
| Age | 46 | 60 | 53 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | In/Line Circulator |  |  |  | Notes
Steam Piping System | Location |  |  |  | IDF #4, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Air Distribution | Location | Typical |  |  | Inter. Data Facility (IDF #5) | Location
| Description | Sheet Metal Ducts |  |  |  | Description
| Age | 46 | 60 | 53 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Air Handling Units | Location | UN/85 |  |  | IDF #5, HVAC Terminal Units | Location
| Description | Indoor Air Handling Units (AHU) |  |  |  | Description
| Age | 40+ |  | 40 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Fans | Location | UN/17 |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  |  | Description
| Age | 40+ |  | 40 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Exhaust Fan |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location | UN/17 |  |  | Backbone Cable Dist. | Location
| Description | Wet/Pipe System |  |  |  | Description
| Age | 0 | 15 | 7.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fire/Suppression (Standpipes), Water/Based | Location | UN/17 |  |  | Horizontal Cable Dist. | Location
| Description | D4020 330 |  |  |  | Description
| Age | 0 | 15 | 7.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 0 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | UN/17
| Description | Gas Engine Generators
| Age | 46 | 60 | 53
| Condition | Very Poor |  | 0.1
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | UN/18
| Description | D5010 120
| Age | 46 | 60 | 53
| Condition | Poor |  | 0.25
CheckBox
| Quantity | 0
| Voltage | 220V
Power Output
Elec Power
Notes
Voice Communication Terminal Equipment | Location | UN/30
| Description | PDX/Key Systems
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | UN/30
| Description | Other (describe)
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
| Notes | Paging, Clock, Public Address and Mass Notification System
Video Surveillance Systems | Location | Entry Lobby #1
| Description | Analog Video Recording Devices
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | UN/17
| Description | Other (describe)
| Age | 0 | 10 | 5
| Condition | Very Good |  | 0.9
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
| Notes | Command Center / Fire/Smoke Detection Sensors w/ Strobe s and Fire Alarm Annunciation Panels
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
Description
Age
Condition
CheckBox
| Quantity | 0
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Exterior | Question | Value1 |  | Average1
Exterior | Seg ID | 216 |  |  | SiteElements | Seg ID | 311
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 0 |  |  |  | Addition | 0
| Year Built |  |  |  |  | Year Built
(Foundation) Walls for Subgrade Enclosures, Primary | Location |  |  |  | Roadways | Location
| Description | Concrete, Cast/In/Place |  |  |  | Description
| Age | 46 | 60 | 53 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location |  |  |  | Parking Lots | Location
| Description |  |  |  |  | Description | Asphalt (Bituminous)
| Age |  |  |  |  | Age | 30+ |  | 30
| Condition |  |  |  |  | Condition | Poor |  | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Standard Slabs On Grade, Primary | Location |  |  |  | Pedestrian Plazas and Walkways, Primary | Location
| Description | Concrete, Cast/In/Place |  |  |  | Description | Concrete, CIP
| Age | 46 | 60 | 53 |  | Age | 30+ |  | 30
| Condition | Fair |  | 0.5 |  | Condition | Poor |  | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Standard Slabs On Grade, Secondary | Location |  |  |  | Pedestrian Plazas and Walkways, Secondary | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Floor Construction, Primary | Location |  |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location
| Description | Concrete, CIP Beams and Slab |  |  |  | Description
| Age | 46 | 60 | 53 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Floor Construction, Secondary | Location |  |  |  | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Roof Construction, Structural Frame, Primary | Location |  |  |  | Site Lighting, Primary | Location
| Description | Concrete, CIP |  |  |  | Description | Pole Mounted H.I.D.
| Age | 46 | 60 | 53 |  | Age | 41136 |  | 11.5
| Condition | Fair |  | 0.5 |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Roof Construction, Structural Frame, Secondary | Location |  |  |  | Site Lighting, Secondary | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Walls / Exterior Assembly, Primary | Location |  |  |  | Playground Surface | Location
| Description | Brick Veneer w/ Steel Stud |  |  |  | Description | Rubberized
| Age | 46 | 60 | 53 |  | Age | 30+ |  | 30
| Condition | Fair |  | 0.5 |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | & Painted Asphalt (Bituminous)
Exterior Walls / Exterior Assembly, Secondary | Location |  |  |  | Playground Equipment | Location
| Description | Stone, Solid (Mass) |  |  |  | Description | Multi/Component Play Equipment Set
| Age | 46 | 60 | 53 |  | Age | 16 | 21 | 18.5
| Condition | Fair |  | 0.5 |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Windows, Primary | Location |  |  |  | TCUs | Location
| Description | Aluminum, Double Hung |  |  |  | Description
| Age | 41136 |  | 11.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Screens, Insect / Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary | Location
| Description | Aluminum, Curtain Wall
| Age | 41136 |  | 11.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
| Description | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location
| Description | Aluminum
| Age | 0 | 15 | 7.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location
| Description | Asphalt, Modified Bitumen
| Age | 41136 |  | 11.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location
| Description | Aluminum
| Age | 41136 |  | 11.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location
| Description | Other (describe)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Internal Gutters
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes