## FCI Summary
Building Name: | 18th Avenue School (Off-Line)
Building Square Footage: | 91215 | 2012 LRFP CONDITION SUMMARY
Number of Floors: | 4
School Age (years): | 89
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 38.32%
Facility Condition = | POOR
FCI Deficiency Cost = | 7208980.1224
FCI Replacement Cost = | 18813093.75
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 0
Historic 2005 LRFP Capacity = | 368
Adjusted 2012 Capacity = | 477
Recent Occupancy % = | 0%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 91.07%
Classroom Adequacy = | GOOD
Special Spaces Adequacy % Score = | 66.44%
Special Spaces Adequacy = | POOR

## Uniformat FCI
Building Name: |  | 18th Avenue School (Off-Line) | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 91215
Largest Floor Level Area: |  | 28644
Vertical FAR Ratio: |  | 3.1844
School Age (years): |  | 89
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 1.8% | 3.7125 | 91215 | 338635.6875 | 100 | 89 | 11 | 0.5 | 50 | 61 | 206567.7694 | 132067.9181 | 39%
|  |  | A1030 - SLAB ON GRADE | 1.5% | 3.0938 | 91215 | 282196.4062 | 100 | 89 | 11 | 0.25 | 25 | 36 | 101590.7063 | 180605.7 | 64%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 91215 | 413888.0625 | 100 | 89 | 11 | 0.5 | 50 | 61 | 252471.7181 | 161416.3444 | 39%
|  |  | SUBTOTAL SUBSTRUCTURE | 5.5% | 11.3438 | 91215 | 1034720.1562
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 91215 | 2069440.3125 | 100 | 89 | 11 | 0.5 | 50 | 61 | 1262358.5906 | 807081.7219 | 39%
|  |  | B1020 - ROOF CONSTRUCTION | 2.5% | 5.1562 | 91215 | 470327.3438 | 100 | 89 | 11 | 0.5 | 50 | 61 | 286899.6797 | 183427.6641 | 39%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 9.5% | 19.5938 | 91215 | 1787243.9062 | 100 | 89 | 11 | 0.50417 | 50.4167 | 61.4167 | 1097665.6324 | 689578.2738 | 38.58%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 5.5% | 11.3438 | 91215 | 1034720.1562 | 30 | 43 | 0 | 0.5 | 5 | 5 | 172453.3594 | 862266.7969 | 83.33%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 2% | 4.125 | 91215 | 376261.875 | 30 | 0 | 30 | 0 | 0 | 30 | 376261.875 | 0 | 0%
|  |  | SUBTOTAL SHELL | 30.5% | 62.9063 | 91215 | 5737993.5938
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 91215 | 752523.75 | 60 | 55.4545 | 4.5455 | 0.50758 | 30.4545 | 35 | 438972.1875 | 313551.5625 | 41.67%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 91215 | 282196.4062 | 20 | 26.1786 | 0 | 0.41071 | 5 | 5 | 70549.1016 | 211647.3047 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 91215 | 752523.75 | 20 | 7.5 | 12.5 | 0.75 | 15 | 20 | 752523.75 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 91215 | 282196.4062 | 30 | 89 | 0 | 0.5 | 5 | 5 | 47032.7344 | 235163.6719 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 4% | 8.25 | 91215 | 752523.75 | 10 | 11.4 | 0 | 0.47143 | 5 | 5 | 376261.875 | 376261.875 | 50%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 91215 | 1128785.625 | 20 | 18.7143 | 1.2857 | 0.37571 | 7.5143 | 8.8 | 496665.675 | 632119.95 | 56%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 91215 | 1128785.625 | 30 | 29.4032 | 0.59677 | 0.5 | 15 | 15.5968 | 586847.1502 | 541938.4748 | 48.01%
|  |  | SUBTOTAL INTERIORS | 27% | 55.6875 | 91215 | 5079535.3125
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 1% | 2.0625 | 91215 | 188130.9375 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 188130.9375 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 91215 | 282196.4062 | 60 | 24.3422 | 35.6578 | 0.53777 | 32.2661 | 60 | 282196.4062 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 91215 | 244570.2188 | 60 | 0 | 60 | 0 | 0 | 60 | 244570.2188 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 91215 | 225757.125 | 60 | 0 | 60 | 0 | 0 | 60 | 225757.125 | 0 | 0%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 91215 | 94065.4688 | 30 | 7.5 | 22.5 | 0.75 | 22.5 | 30 | 94065.4688 | 0 | 0%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 2.7% | 5.5687 | 91215 | 507953.5312 | 60 | 38 | 22 | 0.25 | 15 | 37 | 313238.0109 | 194715.5203 | 38.33%
|  |  | D3020 - BOILERS | 2% | 4.125 | 91215 | 376261.875 | 60 | 38 | 22 | 0.25 | 15 | 37 | 232028.1562 | 144233.7188 | 38.33%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4% | 8.25 | 91215 | 752523.75 | 40 | 29.5 | 10.5 | 0.5 | 20 | 30.5 | 573799.3594 | 178724.3906 | 23.75%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4% | 8.25 | 91215 | 752523.75 | 40 | 21.19 | 18.81 | 0.25 | 10 | 28.81 | 542005.2309 | 210518.5191 | 27.98%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 2% | 4.125 | 91215 | 376261.875 | 40 | 21 | 19 | 0.25 | 10 | 29 | 272789.8594 | 103472.0156 | 27.5%
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.5% | 3.0938 | 91215 | 282196.4062 | 20 | 0 | 20 | 0 | 0 | 20 | 282196.4062 | 0 | 100%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 91215 | 188130.9375 | 20 | 0 | 20 | 0 | 0 | 20 | 188130.9375 | 0 | 100%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 91215 | 37626.1875 | 20 | 3.5 | 16.5 | 0.75 | 15 | 20 | 37626.1875 | 0 | 0%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 91215 | 244570.2188 | 60 | 38 | 22 | 0.25 | 15 | 37 | 150818.3016 | 93751.9172 | 38.33%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 91215 | 1316916.5625 | 30 | 25.3274 | 4.6726 | 0.55655 | 16.6964 | 21.369 | 938041.7578 | 378874.8047 | 28.77%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 91215 | 564392.8125 | 20 | 14.3 | 5.7 | 0.6 | 12 | 17.7 | 499487.6391 | 64905.1734 | 11.5%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 91215 | 56439.2812 | 20 | 23.6293 | 0 | 0.48661 | 5 | 5 | 14109.8203 | 42329.4609 | 75%
|  |  | SUBTOTAL SERVICES | 34.5% | 71.1563 | 91215 | 6490517.3438
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 91215
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 91215
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 91215
|  |  | E1090 - OTHER EQUIPMENT |  |  | 91215
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 91215
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 91215
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 91215
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 91215
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 91215
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 91215 | 188130.9375 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 47032.7344 | 141098.2031 | 75%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 91215 | 94065.4688 | 30 | 30 | 0 | 0.5 | 15 | 15 | 47032.7344 | 47032.7344 | 50%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 91215 | 94065.4688 | 30 | 30 | 0 | 0.5 | 15 | 15 | 47032.7344 | 47032.7344 | 50%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 91215 | 94065.4688 | 30 | 30 | 0 | 0.5 | 15 | 15 | 47032.7344 | 47032.7344 | 50%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 91215 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 91215
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 91215 | 18813093.75 | [7 empty] | 7208980.1224 | 38.32%
100%

## Master File (Interior)
Eighteenth Avenue
School Code: | 380
NPS Code: | 67
Street: | 229 18th Ave.
City/Town: | Newark,
Database ID: | 9
Total size (gsf):
ROOM INFORMATION | [11 empty] | 54.6667 | Ave Condition | 0.50833 | [5 empty] | 18.7143 | Ave Condition | 0.37571 | [6 empty] | 11.4 | Ave Condition | 0.47143 | [5 empty] | 29.4032 | Ave Condition | 0.5 | [5 empty] | 26.1786 | Ave Condition | 0.41071 | [5 empty] | 55.4545 | Ave Condition | 0.50758 | [6 empty] | 26.9062 | Ave Condition | 0.45312 | [5 empty] | 22.0714 | Ave Condition | 0.57143 | [5 empty] | 23.8333 | Ave Condition | 0.51429 | [5 empty] | 30 | Ave Condition | 0.5 | [5 empty] | 18.9 | Ave Condition | 0.65 | [6 empty] | 7.5 | Ave Condition | 0.75 | [6 empty] | 15.9821 | Ave Condition | 0.66964 | [5 empty] | 24.2586 | Ave Condition | 0.47321 | [6 empty] | 29.08 | Ave Condition | 0.25 | [6 empty] | 13.3 | Ave Condition | 0.25 | [6 empty] | 3.5 | Ave Condition | 0.75 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 10 | Ave Condition | 0.5 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [7 empty] | Floor Finish | [7 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Interior Door | [7 empty] | Partitions | [7 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [7 empty] | Plumbing Fixtures - Urinals | [7 empty] | Plumbing Fixtures - Showers | [7 empty] | Plumbing Fixtures - Drinking Fountains | [7 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [7 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
3737 | 111 | Classroom | 1st Floor | A | Pre-Kindergarten Classroom |  |  | 1380 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3738 | 112 | Classroom | 1st Floor | A | Pre-Kindergarten Classroom |  |  | 563 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3739 | 113 | Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 720 | 12' 5" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3740 | 114 | Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 464 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3741 | 115 | Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 516 | 12' | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Other (describe) | 60+ | 60 | Good | 0.75 | 0 | [8 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  | ducted central air conditioning | [25 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present
3742 | UN-1 | Principal's Office | 1st Floor | A | Administration |  |  | 209 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3743 | UN-2 | Main Office | 1st Floor | A | Administration |  |  | 549 | 12' | Plaster on Metal Lath | 60+ | 60 | Poor | 0.25 |  |  | Water damage | Vinyl Composition Tile (VCT) | 20+ | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ | 30 | Poor | 0.25 |  |  | Water damage | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ | 60 | Fair | 0.5 |  |  | Plaster on cmu | [50 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 |  |  |  | Window Mounted | 22 | 30 | 26 | Poor | 0.25 | [19 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present | Headend paging
3744 | UN-3 | N/A | 1st Floor | A | N/A |  |  | 59 | N/A
3745 | UN-4 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 109 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3746 | UN-5 | Storage | 1st Floor | A | Support |  |  | 129 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3747 | UN-6 | N/A | 1st Floor | A | Support |  |  | 12 | N/A
3748 | UN-7 | Auditorium | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 3546 | 24' | Plaster Partitions/Metal Stud Framing | 60+ | 60 | Good | 0.75 |  |  |  | Epoxy | 41228 | 13 | Good | 0.75 |  |  |  | Painted Walls | 41100 |  | 8.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | [7 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Good | 0.75 | [53 empty] | Incandescent Pendant Mount Fixture | 30+ |  | 30 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | [28 empty] | Present - Present - Present - Present - Present | [133 empty] | Present - Present - Present - Present
3749 | UN-8 | N/A | 1st Floor | A | N/A |  |  | 109 | N/A
3750 | UN-9 | N/A | 1st Floor | A | N/A |  |  | 176 | N/A
3751 | UN-10 | N/A | 1st Floor | A | N/A |  |  | 55 | N/A
3752 | UN-11 | Storage | 1st Floor | A | Pre-Kindergarten Classroom |  |  | 144 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3753 | UN-12 | Storage | 1st Floor | A | Pre-Kindergarten Classroom |  |  | 78 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3754 | UN-13 | Storage | 1st Floor | A | Kindergarten Classroom |  |  | 77 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3755 | UN-14 | Storage | 1st Floor | A | Kindergarten Classroom |  |  | 80 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3756 | UN-15 | N/A | 1st Floor | A | N/A |  |  | 64 | N/A
3757 | UN-16 | Storage | 1st Floor | A | Support |  |  | 74 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3758 | UN-17 | Storage | 1st Floor | A | Support |  |  | 115 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3759 | UN-18 | Storage | 1st Floor | A | Support |  |  | 110 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3760 | UN-19 | Storage | 1st Floor | A | Support |  |  | 119 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3761 | UN-20 | Fan Room | 1st Floor | A | Support |  |  | 296 | 12' | [8 empty] | Unfinished | [16 empty] | Acoustical Panel
3762 | UN-21 | N/A | 1st Floor | A | Pre-Kindergarten Classroom |  |  | 14 | N/A
3763 | UN-22 | N/A | 1st Floor | A | N/A |  |  | 149 | N/A
3764 | UN-23 | Faculty Water Closet | 1st Floor | A | Pre-Kindergarten Classroom |  |  | 167 | 12' 2" | [8 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [29 empty] | 2 | [7 empty] | 2 | [7 empty] | 0
3765 | UN-24 | Food Pantry | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 780 | 13' 6" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3766 | UN-25 | Kitchen | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 687 | 13' 6" | Plaster Partitions/on CMU Back-up Wall | 60+ | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ | 60 | Poor | 0.25 |  |  | Plaster on masonry | Stainless Steel Sinks | 16 | 21 | 18.5 | Fair | 0.5 | 3 |  | Plus one hand sink. 30+. Poor | [41 empty] | Fluorescent Linear Pendant Mount Fixture | 30+ |  | 30 | Poor | 0.25 |  |  |  | Keyed Wall Switches | 30+ | 30 | [5 empty] | Terminal Unit Heaters | 16 | 21 | 18.5 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Kitchen exhaust fan | [16 empty] | Present - Present | [133 empty] | Present - Present | [26 empty] | Present | [8 empty] | Present
3767 | UN-26 | Storage | 1st Floor | A | Support |  |  | 57 | 13' 6" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3768 | UN-27 | Storage | 1st Floor | A | Support |  |  | 40 | 13' 6" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3769 | UN-28 | Cafeteria | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 2741 | 12' 5"
3770 | UN-29 | Custodial Office | 1st Floor | A | Support |  |  | 65 | 12' | Plaster Partitions/on CMU Back-up Wall | 60+ | 60 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ | 30 | Poor | 0.25 |  |  |  | Metal/Metal Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ | 60 | Poor | 0.25 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 |  |  |  | Floor Mounted Flush Valve | 30+ | 30 | Poor | 0.25 | [6 empty] | Very Poor | 0.1 |  |  | Shower | [25 empty] | Fluorescent Recessed Fixture | 30+ |  | 30 | Poor | 0.25 |  |  |  | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | [28 empty] | Present - Present - Present | [133 empty] | Present - Present - Present
3771 | UN-30 | Boys' Water Closet | 1st Floor | A | Support |  |  | 89 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel | [29 empty] | 2 | [7 empty] | 2 | [7 empty] | 2
3772 | UN-31 | Storage | 1st Floor | A | Support |  |  | 79 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3773 | UN-32 | N/A | 1st Floor | A | N/A |  |  | 13 | N/A
3774 | UN-33 | Girls' Water Closet | 1st Floor | A | Support |  |  | 148 | 12' | [8 empty] | Ceramic Tile | [16 empty] | Acoustical Panel | [29 empty] | 2 | [7 empty] | 5 | [7 empty] | 0
3775 | UN-34 | Storage | 1st Floor | A | Health Services |  |  | 22 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3776 | UN-35 | Nurse\'s Office | 1st Floor | A | Health Services |  |  | 310 | 12' | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 |  |  | radiant pipes | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | [19 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present
3777 | UN-36 | Storage | 1st Floor | A | Health Services |  |  | 104 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3778 | UN-37 | Storage | 1st Floor | A | Health Services |  |  | 336 | 10' 7" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | [9 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 |  |  | radiant pipes | [25 empty] | Present - Present - Present
3779 | UN-38 | Meter Room | 1st Floor | A | Support |  |  | 748 | 12' | [8 empty] | Unfinished | [16 empty] | Acoustical Panel
3780 | UN-39 | Storage | 1st Floor | A | Support |  |  | 211 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3781 | UN-40 | Storage | 1st Floor | A | Support |  |  | 138 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3782 | UN-41 | Storage | 1st Floor | A | Support |  |  | 285 | 6' 11" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3783 | UN-42 | N/A | 1st Floor | A | Support |  |  | 668 | N/A
3784 | UN-43 | Custodial Office | 1st Floor | A | Support |  |  | 258 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3785 | UN-44 | N/A | 1st Floor | A | N/A |  |  | 103 | N/A
3786 | UN-45 | N/A | 1st Floor | A | N/A |  |  | 82 | N/A
3787 | UN-46 | N/A | 1st Floor | A | N/A |  |  | 137 | N/A
3788 | UN-47 | Gymnasium | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 3734 | 27' 5"/12' 5" | [8 empty] | Epoxy | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41100 |  | 8.5 | Fair | 0.5 |  |  |  | Unfinished Ceiling | 41136 | 11.5 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Other (describe) | 60+ | 60 | Poor | 0.25 |  |  | Brick | [50 empty] | HID Vapor Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Other (describe) | 16 | 21 | 18.5 | Good | 0.75 |  |  | Ducted supply | [25 empty] | Present - Present - Present - Present
3789 | 201 | Classroom | 2nd Floor | A | General Classroom |  |  | 778 | 11' 11" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3790 | 202 | 1st Grade | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 804 | 11' 11" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3791 | 203 | Empty | 2nd Floor | A | N/A |  |  | 804 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3792 | 204 | Special Education 1st-3rd | 2nd Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 804 | 11' 11" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3793 | 205 | 2nd Grade | 2nd Floor | A | General Classroom (Grades 1-3) |  |  | 780 | 12' 2" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ | 30 | Poor | 0.25 | 0 | [10 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present
3794 | 206 | Reading Tutor | 2nd Floor | A | Small Group Instruction |  |  | 821 | 12' 2" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 | [10 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present
3795 | 207 | Kindergarten | 2nd Floor | A | Kindergarten Classroom |  |  | 821 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3796 | 208 | Kindergarten | 2nd Floor | A | Kindergarten Classroom |  |  | 821 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3797 | 209 | Faculty Room | 2nd Floor | A | Faculty Support |  |  | 780 | 12' 1" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 |  |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 3 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 |  |  |  | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present
3798 | 210 | Library | 2nd Floor | A | Media Center |  |  | 1032 | 11' 8" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 | 13 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 | [10 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present - Present
3799 | 211 | Server Room | 2nd Floor | A | Technological Literacy |  |  | 254 | 11' 8" | [8 empty] | Carpet | [16 empty] | Acoustical Panel
3800 | 212 | Computer Lab | 2nd Floor | A | Technological Literacy |  |  | 559 | 11' 8" | [8 empty] | Carpet | [16 empty] | Acoustical Panel
3801 | 213 | Literacy Coach | 2nd Floor | A | Small Group Instruction |  |  | 705 | 11' 8" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ | 20 | Very Poor | 0.1 | 0 |  | major cracking | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 1 |  | wall mounted stainless steel | [41 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present - Present - Present
3802 | UN-48 | N/A | 2nd Floor | A | N/A |  |  | 143 | N/A
3803 | UN-49 | N/A | 2nd Floor | A | Food Service/Assembly (K-8) |  |  | 71 | N/A
3804 | UN-50 | Balcony | 2nd Floor | A | Food Service/Assembly (K-8) |  |  | 390 | 11' 5" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Unfinished | 20+ | 20 | Fair | 0.5 |  |  | exposed concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Good | 0.75 | [9 empty] | 0 | [43 empty] | Incandescent Surface Mount Fixture | 30+ |  | 30 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | heating and ventilating vent | [25 empty] | Present - Present - Present - Present - Present - Present
3805 | UN-51 | Booth Room | 2nd Floor | A | Food Service/Assembly (K-8) |  |  | 119 | N/A | [8 empty] | Other (describe) | 20+ | 20 | Fair | 0.5 |  |  | exposed concrete | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | painted concrete | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | [9 empty] | 0 | [43 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | projector exhaust duct
3806 | UN-52 | N/A | 2nd Floor | A | Food Service/Assembly (K-8) |  |  | 93 | N/A
3807 | UN-53 | N/A | 2nd Floor | A | N/A |  |  | 296 | N/A
3808 | UN-54 | Counselor's Office | 2nd Floor | A | Administration |  |  | 232 | 8' 8" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3809 | UN-55 | Counselor's Water Closet | 2nd Floor | A | Administration |  |  | 26 | N/A | [55 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
3810 | UN-55 | N/A | 2nd Floor | A | Support |  |  | 108 | N/A
3811 | UN-56 | Custodial Closet | 2nd Floor | A | Support |  |  | 45 | N/A | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Other (describe) | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  | painted concrete | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 1 |  | mop sink | [5 empty] | 0 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 | [37 empty] | Present - Present - Present - Present - Present - Present - Present
3812 | UN-57 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 209 | N/A | [8 empty] | Ceramic Tile | [16 empty] | Plaster | [29 empty] | 2 | [7 empty] | 4 | [7 empty] | 6
3813 | UN-58 | Storage | 2nd Floor | A | Media Center |  |  | 149 | N/A | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 41228 | 13 | Good | 0.75 |  |  |  | Drywall (Gypsum)/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [43 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0
3814 | UN-59 | Storage | 2nd Floor | A | Media Center |  |  | 149 | N/A
3815 | UN-60 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 118 | N/A | [8 empty] | Ceramic Tile | [16 empty] | Plaster | [29 empty] | 3 | [7 empty] | 3 | [7 empty] | 3
3816 | UN-61 | N/A | 2nd Floor | A | Support |  |  | 26 | N/A
3817 | UN-62 | Faculty Water Closet | 2nd Floor | A | Faculty Support |  |  | 12 | N/A | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Other (describe) | 20+ | 20 | Poor | 0.25 |  |  | painted concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  |  | Floor Mounted Flush Tank | 30+ | 30 | Fair | 0.5 | 1 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Surface Mount Fixture | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5
3818 | UN-63 | Faculty Lounge | 2nd Floor | A | Faculty Support |  |  | 278 | 12' 4" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | [9 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present - Present - Present
3819 | UN-64 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 136 | N/A | [55 empty] | 2 | [7 empty] | 4 | [7 empty] | 0
3820 | UN-65 | Custodial Closet | 2nd Floor | A | Support |  |  | 13 | N/A
3821 | UN-66 | Storage | 2nd Floor | A | Support |  |  | 265 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3822 | UN-67 | N/A | 2nd Floor | A | Support |  |  | 137 | N/A
3823 | UN-68 | Child Study Team | 2nd Floor | A | Administration |  |  | 137 | N/A | [25 empty] | Acoustical Panel
3824 | 301 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 778 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3825 | 302 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 804 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3826 | 303 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 804 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3827 | 304 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 804 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3828 | 305 | Classroom | 3rd Floor | A | General Classroom (Grades 1-3) |  |  | 780 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3829 | 306 | Classroom | 3rd Floor | A | General Classroom (Grades 1-3) |  |  | 821 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3830 | 307 | Resource Room | 3rd Floor | A | Administration |  |  | 821 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | [29 empty] | 0 | [52 empty] | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | [37 empty] | Present | [133 empty] | Present
3831 | 308 | Classroom | 3rd Floor | A | General Classroom (Grades 1-3) |  |  | 821 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3832 | 309 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 780 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3833 | 310 | Classroom | 3rd Floor | A | General Classroom |  |  | 804 | 11' 9" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3834 | 311 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 804 | 11' 9" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present
3835 | 312 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 804 | 11' 9" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3836 | 313 | Classroom | 3rd Floor | A | General Classroom (Grades 4-5) |  |  | 705 | 11' 9" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3837 | S | N/A | 3rd Floor | A | Support |  |  | 151 | N/A
3838 | S | N/A | 3rd Floor | A | Support |  |  | 107 | N/A
3839 | UN-69 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 55 | N/A
3840 | UN-70 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 68 | N/A
3841 | UN-71 | Gymnasium | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 3101 | 21' 2" | Brick, Exposed/Unfinished | 60+ | 60 | Poor | 0.25 |  |  |  | Wood | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Other (describe) | 60+ | 60 | Fair | 0.5 |  |  | brick | [6 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | HID Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  | recessed | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | [28 empty] | Present - Present - Present | [42 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present
3842 | UN-72 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 77 | N/A
3843 | UN-73 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 43 | N/A
3844 | UN-74 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 44 | N/A
3845 | UN-75 | N/A | 3rd Floor | A | Phys. Ed. (Gym + Storage) |  |  | 169 | N/A | [8 empty] | Wood | 20+ | 20 | Poor | 0.25 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | [9 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | Incandescent Surface Mount Fixture | 30+ |  | 30 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | exhaust grille | [68 empty] | 0 | [8 empty] | 0 | [8 empty] | 0
3846 | UN-76 | storage | 3rd Floor | A | Support |  |  | 289 | N/A
3847 | UN-77 | N/A | 3rd Floor | A | N/A |  |  | 143 | N/A
3848 | UN-78 | N/A | 3rd Floor | A | N/A |  |  | 421 | N/A
3849 | UN-79 | N/A | 3rd Floor | A | Support |  |  | 158 | N/A
3850 | UN-80 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 118 | N/A | [8 empty] | Ceramic Tile | [16 empty] | Plaster | [29 empty] | 3 | [7 empty] | 3 | [7 empty] | 3
3851 | UN-81 | N/A | 3rd Floor | A | N/A |  |  | 26 | N/A
3852 | UN-82 | Faculty Lounge | 3rd Floor | A | Faculty Support |  |  | 278 | 12' | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Acoustical Panel
3853 | UN-83 | Faculty Water Closet | 3rd Floor | A | Faculty Support |  |  | 12 | N/A | [55 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
3854 | UN-84 | Custodial Closet | 3rd Floor | A | Support |  |  | 13 | N/A
3855 | UN-85 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 136 | N/A | [8 empty] | Ceramic Tile | [16 empty] | Plaster | [29 empty] | 2 | [7 empty] | 4 | [7 empty] | 0
3856 | UN-86 | Speech Therapy | 3rd Floor | A | Small Group Instruction |  |  | 137 | N/A
3857 | UN-87 | Psychologist Room | 3rd Floor | A | Administration |  |  | 137 | N/A
3858 | 401 | Music Room | 4th Floor | A | Visual & Performing Arts |  |  | 778 | 12' 2" | [8 empty] | Wood | [16 empty] | Plaster | 30+ | 30 | Poor | 0.25 |  |  | plaster damage over entrance door | [22 empty] | 0 | [52 empty] | Toggle Wall Switches | 30+ | 30 | Poor | 0.25 | [37 empty] | Present | [133 empty] | Present
3859 | 402 | Empty | 4th Floor | A | N/A |  |  | 804 | 12' | [8 empty] | Wood | [16 empty] | Plaster
3860 | 403 | Science Lab | 4th Floor | A | Science (6-12) |  |  | 804 | 12' | Plaster on Metal Lath | 60+ | 60 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ | 30 | Poor | 0.25 | 0 | [10 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present
3861 | 404 | Math 7th/8th | 4th Floor | A | General Classroom (Grades 6-8) |  |  | 804 | 12' | [8 empty] | Wood | [16 empty] | Plaster
3862 | 405 | Special Education 6th/8th | 4th Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 780 | 12' 2" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3863 | 406 | Read 180 | 4th Floor | A | General Classroom |  |  | 821 | 12' | [8 empty] | Wood | [16 empty] | Plaster
3864 | 407 | Literature 7th/8th | 4th Floor | A | General Classroom (Grades 6-8) |  |  | 821 | 12' | [8 empty] | Wood | [16 empty] | Plaster
3865 | 408 | Math 6th | 4th Floor | A | General Classroom (Grades 6-8) |  |  | 821 | 12' | [8 empty] | Wood | [16 empty] | Plaster
3866 | 409 | Art Room | 4th Floor | A | Visual & Performing Arts |  |  | 780 | 12' | [8 empty] | Wood | [16 empty] | Plaster
3867 | 410 | Classroom | 4th Floor | A | General Classroom (Grades 6-8) |  |  | 804 | 11' 9" | [8 empty] | Wood | [16 empty] | Plaster
3868 | 411 | Special Education Classroom | 4th Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 804 | 11' 9" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Poor | 0.25 | 0 |  | water damage | [8 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 41136 | 11.5 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present
3869 | 412 | Guidance Office | 4th Floor | A | Administration |  |  | 456 | 11' 9" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Wood | 20+ | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 41136 | 11.5 | Good | 0.75 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Good | 0.75 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | [19 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | [111 empty] | Present - Present - Present - Present
3870 | 413 | Faculty Resource Room | 4th Floor | A | Administration |  |  | 705 | 11' 9" | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Wood | 20+ | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present - Present
3871 | M | Storage | 4th Floor | A | Support |  |  | 24 | N/A | [8 empty] | Unfinished | 20+ | 20 | Fair | 0.5 |  |  | exposed concrete | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | [9 empty] | 0 | [7 empty] | 0 | [7 empty] | 0 | [27 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | [45 empty] | Present - Present - Present - Present - Present - Present
3872 | M | N/A | 4th Floor | A | Support |  |  | 32 | N/A
3873 | M | N/A | 4th Floor | A | Support |  |  | 189 | N/A
3874 | P | N/A | 4th Floor | A | Support |  |  | 61 | N/A
3875 | P | N/A | 4th Floor | A | Support |  |  | 50 | N/A
3876 | P | N/A | 4th Floor | A | Support |  |  | 37 | N/A
3877 | UN-88 | N/A | 4th Floor | A | N/A |  |  | 143 | N/A
3878 | UN-89 | N/A | 4th Floor | A | N/A |  |  | 76 | N/A
3879 | UN-90 | N/A | 4th Floor | A | N/A |  |  | 54 | N/A
3880 | UN-91 | Balcony | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 429 | N/A
3881 | UN-92 | Balcony | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 690 | N/A
3882 | UN-93 | N/A | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 32 | N/A
3883 | UN-94 | N/A | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 54 | N/A
3884 | UN-95 | Storage | 4th Floor | A | Support |  |  | 23 | N/A
3885 | UN-96 | N/A | 4th Floor | A | Administration |  |  | 23 | N/A
3886 | UN-97 | Girls\' Water Closet | 4th Floor | A | Support |  |  | 212 | N/A | Plaster on Metal Lath | 60+ | 60 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ | 20 | Poor | 0.25 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | paint cracking | Plaster | 30+ | 30 | Poor | 0.25 |  |  |  | Wood/Metal Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ | 60 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 22 | 30 | 26 | Fair | 0.5 | 3 |  |  | Floor Mounted Flush Valve | 30+ | 30 | Fair | 0.5 | 6 | [7 empty] | 0 | [18 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 41136 | 11.5 | Good | 0.75 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present - Present - Present - Present - Present
3887 | UN-98 | N/A | 4th Floor | A | Administration |  |  | 23 | N/A
3888 | UN-99 | N/A | 4th Floor | A | Administration |  |  | 23 | N/A
3889 | UN-100 | Faculty Water Closet | 4th Floor | A | Faculty Support |  |  | 12 | N/A | [55 empty] | 1 | [7 empty] | 1 | [7 empty] | 0
3890 | UN-101 | Boys' Water Closet | 4th Floor | A | Support |  |  | 118 | N/A | [55 empty] | 2 | [7 empty] | 3 | [7 empty] | 3
3891 | UN-102 | N/A | 4th Floor | A | N/A |  |  | 42 | N/A
3892 | UN-103 | Faculty Lounge | 4th Floor | A | Faculty Support |  |  | 278 | 12' 4" | [8 empty] | Vinyl Composition Tile (VCT) | [16 empty] | Plaster
3893 | UN-104 | Girls' Water Closet | 4th Floor | A | Support |  |  | 136 | N/A | [8 empty] | Ceramic Tile | [16 empty] | Plaster | [29 empty] | 2 | [7 empty] | 4 | [7 empty] | 0
3894 | UN-105 | Custodial Closet | 4th Floor | A | Support |  |  | 42 | N/A
3895 | UN-106 | N/A | 4th Floor | A | N/A |  |  | 137 | N/A
3896 | UN-107 | N/A | 4th Floor | A | N/A |  |  | 137 | N/A
INTERIORs INFORMATION
Corridors | [9 empty] | Floor Finish | [7 empty] | Wall Finish | [7 empty] | Ceiling Finish | [8 empty] | Standpipes | [7 empty] | Partitions | [7 empty] | Plumbing Fixtures - Drinking Fountains | [7 empty] | Lockers | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [7 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
193 | A |  | 1st | [6 empty] | Epoxy | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | [11 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 |  |  |  | Wall Mounted Stainless Steel Drinking Fountains | 30+ | 30 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 41136 | 11.5 | Good | 0.75 |  |  | Water | [7 empty] | Present | [16 empty] | Present | [8 empty] | Present
194 | B |  | 1st | [6 empty] | Epoxy | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 | 4.5 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | [11 empty] | Plaster/Wood Stud Framing | 60+ | 60 | Fair | 0.5 |  |  |  | Wall Mounted Stainless Steel Drinking Fountains | 30+ | 30 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 41136 | 11.5 | Good | 0.75 |  |  | Water | [7 empty] | Present | [16 empty] | Present | [8 empty] | Present
195 | C |  | 1st | [6 empty] | Epoxy | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | [11 empty] | Other (describe) | 60+ | 60 | Fair | 0.5 |  |  | Plaster on brick | [17 empty] | Fluorescent Linear Surface Mount Fixture | 30+ | 30 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 41136 | 11.5 | Good | 0.75 |  |  | Water | [7 empty] | Present | [16 empty] | Present | [8 empty] | Present
196 | D |  | 1st | [6 empty] | Epoxy | 20+ | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ | 10 | Poor | 0.25 |  |  |  | Unfinished Ceiling | 30+ |  | 30 | Fair | 0.5 | [11 empty] | Other (describe) | 60+ | 60 | Fair | 0.5 |  |  | Plaster on brick | Wall Mounted Stainless Steel Drinking Fountains | 30+ | 30 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [18 empty] | Present | [16 empty] | Present | [8 empty] | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [7 empty] | Stair Construction | [7 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Tread Finish | [7 empty] | Landing Finish | [7 empty] | Interior Door | [8 empty] | Standpipes | [7 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [7 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
183 | A |  | 1st | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 60+ | 60 | Good | 0.75 |  |  |  | Reinforced Concrete | 30+ | 30 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Exposed Concrete | 30+ | 30 | Fair | 0.5 |  |  | Epoxy | Exposed Concrete | 30+ | 30 | Fair | 0.5 |  |  | Epoxy | Metal/Metal Frame | 41228 |  | 13 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [19 empty] | Present
184 | B |  | 1st | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 60+ | 60 | Fair | 0.5 |  |  |  | Reinforced Concrete | 30+ | 30 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Exposed Concrete | 30+ | 30 | Poor | 0.25 |  |  | Epoxy | Exposed Concrete | 30+ | 30 | Poor | 0.25 |  |  | Epoxy | Metal/Metal Frame | 41228 |  | 13 | Good | 0.75 | [11 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [19 empty] | Present

## Master File (Systems)
Systems | Question | Value1 |  | Average1 | Systems | Question | Value1 | Average1
Systems | Seg ID | 1679 |  |  | InfoTech | Seg ID | 527
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 0 |  |  |  | Addition | 0
| Year Built | 1923 |  |  |  | Year Built | 1923
Domestic Water Heaters | Location |  |  |  | Entrance Facilities (Demarc or Cable Vault) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Sanitary Drainage | Location |  |  |  | Main Dist. Facility (MDF) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Building Support (other) Plumbing Systems | Location |  |  |  | MDF, HVAC Terminal Units | Location
| Description | Stormwater Area Drains |  |  |  | Description
| Age | 0 | 15 | 7.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Piping | Location |  |  |  | MDF, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Pumps | Location |  |  |  | Inter. Data Facility (IDF #1) | Location
| Description | Fuel/Oil Pumps |  |  |  | Description | Un/5
| Age | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | None
Fuel Storage Tanks | Location |  |  |  | IDF #1, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fuel Fired Boilers | Location | Boiler room |  |  | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Oil/Fired Boilers |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Furnaces | Location |  |  |  | Inter. Data Facility (IDF #2) | Location
| Description |  |  |  |  | Description | 212
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | None
Unit Ventilators | Location |  |  |  | IDF #2, HVAC Terminal Units | Location
| Description |  |  |  |  | Description | Cast Iron Radiators
| Age |  |  |  |  | Age | 30+ | 30
| Condition |  |  |  |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fan Coil Units | Location |  |  |  | IDF #2, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description | Window Mounted
| Age |  |  |  |  | Age | 41136 | 11.5
| Condition |  |  |  |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Water Chillers | Location |  |  |  | Inter. Data Facility (IDF #3) | Location
| Description |  |  |  |  | Description | Un/73
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | None
Cooling Towers | Location |  |  |  | IDF #3, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Packaged Terminal Air Conditioner | Location |  |  |  | IDF #3, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Hydronic Piping System | Location |  |  |  | Inter. Data Facility (IDF #4) | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Pumps | Location |  |  |  | IDF #4, HVAC Terminal Units | Location
| Description | Steam Condensate Pumps |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Boiler |  |  |  | Notes
Steam Piping System | Location |  |  |  | IDF #4, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Air Distribution | Location |  |  |  | Inter. Data Facility (IDF #5) | Location
| Description | Exhaust Air Grilles (Ducted) |  |  |  | Description
| Age | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Centrifical exhaust fans |  |  |  | Notes
Air Handling Units | Location | Un/20@ |  |  | IDF #5, HVAC Terminal Units | Location
| Description | Indoor Air Handling Units (AHU) |  |  |  | Description
| Age | 41233 |  | 10.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity | 1 |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
HVAC Fans | Location |  |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description | Hooded Roof Ventilators |  |  |  | Description
| Age | 40+ |  | 40 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location |  |  |  | Backbone Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fire/Suppression (Standpipes), Water/Based | Location |  |  |  | Horizontal Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Facility Power Generation, Packaged Generator Assemblies | Location
| Description | Gas Engine Generators
| Age | 16 | 30 | 23
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location
| Description | D5010 120
| Age | 31 | 45 | 38
| Condition | Poor |  | 0.25
CheckBox
Quantity
| Voltage | 700
Power Output
Elec Power
Notes
Voice Communication Terminal Equipment | Location | Un/33, not un/27
| Description | PDX/Key Systems
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | Un/2
| Description | Public Address and Mass Notification Systems
| Age | 31 | 40 | 35.5
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Video Surveillance Systems | Location
| Description | Digital Video Recorders
| Age | 41233 |  | 10.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location
| Description | Fire Alarm Annunciation Panels
| Age | 41233 |  | 10.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Exterior | Question | Value1 | Average1
Exterior | Seg ID | 2087 |  |  | SiteElements | Seg ID | 484
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 0 |  |  |  | Addition | 0
| Year Built | 1923 |  |  |  | Year Built | 1923
(Foundation) Walls for Subgrade Enclosures, Primary | Location | Boiler |  |  | Roadways | Location | West
| Description | CMU, Regular |  |  |  | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 |  | Condition | Poor | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location |  |  |  | Parking Lots | Location | West
| Description |  |  |  |  | Description | Asphalt (Bituminous)
| Age |  |  |  |  | Age | 30+ | 30
| Condition |  |  |  |  | Condition | Poor | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Standard Slabs On Grade, Primary | Location | Boiler |  |  | Pedestrian Plazas and Walkways, Primary | Location | East
| Description | Concrete, Cast/In/Place |  |  |  | Description | Concrete, CIP
| Age | 60+ |  | 60 |  | Age | 30+ | 30
| Condition | Poor |  | 0.25 |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Standard Slabs On Grade, Secondary | Location |  |  |  | Pedestrian Plazas and Walkways, Secondary | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Floor Construction, Primary | Location | Boiler |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location | South
| Description | Other (describe) |  |  |  | Description | Other (describe)
| Age | 60+ |  | 60 |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 |  | Condition | Poor | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Clay tiles arch |  |  |  | Notes | Asphalt
Floor Construction, Secondary | Location |  |  |  | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Roof Construction, Structural Frame, Primary | Location |  |  |  | Site Lighting, Primary | Location | Typ
| Description |  |  |  |  | Description | Pole Mounted H.I.D.
| Age |  |  |  |  | Age | 30+ | 30
| Condition |  |  |  |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Roof Construction, Structural Frame, Secondary | Location |  |  |  | Site Lighting, Secondary | Location | Typ
| Description |  |  |  |  | Description | Building Mounted H.I.D.
| Age |  |  |  |  | Age | 30+ | 30
| Condition |  |  |  |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Walls / Exterior Assembly, Primary | Location | Typ |  |  | Playground Surface | Location | Typ
| Description | Brick, Solid (Mass) |  |  |  | Description | Rubberized
| Age | 60+ |  | 60 |  | Age | 30+ | 30
| Condition | Fair |  | 0.5 |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Walls / Exterior Assembly, Secondary | Location |  |  |  | Playground Equipment | Location | Typ
| Description |  |  |  |  | Description | Multi/Component Play Equipment Set
| Age |  |  |  |  | Age | 30+ | 30
| Condition |  |  |  |  | Condition | Fair | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Windows, Primary | Location | Typ |  |  | TCUs | Location
| Description | Aluminum, Double Hung |  |  |  | Description
| Age | 22 | 30 | 26 |  | Age
| Condition | Fair |  | 0.5 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Security Grilles
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location | Typ
| Description | Fiber Reinforced Panel (FRP)
| Age | 60+ |  | 60
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes