## FCI Summary
Building Name: | Avon Avenue (Brick-Avon Academy) | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 91081
Number of Floors: | B + 3
School Age (years): | ##
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 26.19%
Facility Condition = | FAIR
FCI Deficiency Cost = | 4919239.8555
FCI Replacement Cost = | 18785456.25
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 584
Historic 2005 LRFP Capacity = | 513
Adjusted 2012 Capacity = | 598
Recent Occupancy % = | 97.66%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 91.57%
Classroom Adequacy = | GOOD
Special Spaces Adequacy % Score = | 69.3%
Special Spaces Adequacy = | POOR

## Uniformat FCI
Building Name: |  | Avon Avenue (Brick-Avon Academy) | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 91081
Largest Floor Level Area: |  | 27495
Vertical FAR Ratio: |  | 3.3126
School Age (years): |  | ##
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 1.8% | 3.7125 | 91081 | 338138.2125 | 100 | 110 | 0 | 0.5 | 5 | 5 | 16906.9106 | 321231.3019 | 95%
|  |  | A1030 - SLAB ON GRADE | 1.5% | 3.0938 | 91081 | 281781.8438 | 100 | 49 | 51 | 0.625 | 62.5 | 100 | 281781.8438 | 0 | 0%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 91081 | 413280.0375 | 100 | 49 | 51 | 0.625 | 62.5 | 100 | 413280.0375 | 0 | 0%
|  |  | SUBTOTAL SUBSTRUCTURE | 5.5% | 11.3438 | 91081 | 1033200.0938
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 91081 | 2066400.1875 | 100 | 49 | 51 | 0.625 | 62.5 | 100 | 2066400.1875 | 0 | 0%
|  |  | B1020 - ROOF CONSTRUCTION | 2.5% | 5.1562 | 91081 | 469636.4062 | 100 | 49 | 51 | 0.625 | 62.5 | 100 | 469636.4062 | 0 | 0%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 9.5% | 19.5938 | 91081 | 1784618.3438 | 100 | 56.8571 | 43.1429 | 0.37857 | 37.8571 | 81 | 1445540.8584 | 339077.4853 | 19%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 5.5% | 11.3438 | 91081 | 1033200.0938 | 30 | 14.125 | 15.875 | 0.5 | 15 | 30 | 1033200.0938 | 0 | 0%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 2% | 4.125 | 91081 | 375709.125 | 30 | 21.1667 | 8.8333 | 0.75 | 22.5 | 30 | 375709.125 | 0 | 0%
|  |  | SUBTOTAL SHELL | 30.5% | 62.9063 | 91081 | 5729564.1563
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 91081 | 751418.25 | 60 | 51.7059 | 8.2941 | 0.50735 | 30.4412 | 38.7353 | 485106.782 | 266311.468 | 35.44%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 91081 | 281781.8438 | 20 | 23.4706 | 0 | 0.47429 | 5 | 5 | 70445.4609 | 211336.3828 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 91081 | 751418.25 | 20 | 7.5 | 12.5 | 0.75 | 15 | 20 | 751418.25 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 91081 | 281781.8438 | 30 | 110 | 0 | 0.5 | 5 | 5 | 46963.6406 | 234818.2031 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 4% | 8.25 | 91081 | 751418.25 | 10 | 8.3611 | 1.6389 | 0.56528 | 5.6528 | 7.2917 | 547909.1406 | 203509.1094 | 27.08%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 91081 | 1127127.375 | 20 | 18.9028 | 1.0972 | 0.30139 | 6.0278 | 7.125 | 401539.1273 | 725588.2477 | 64.38%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 91081 | 1127127.375 | 30 | 26.4242 | 3.5758 | 0.50152 | 15.0455 | 18.6212 | 699615.9312 | 427511.4438 | 37.93%
|  |  | SUBTOTAL INTERIORS | 27% | 55.6875 | 91081 | 5072073.1875
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 1% | 2.0625 | 91081 | 187854.5625 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 187854.5625 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 91081 | 281781.8438 | 60 | 25.9117 | 34.0883 | 0.46208 | 27.725 | 60 | 281781.8438 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 91081 | 244210.9312 | 60 | 18.5 | 41.5 | 0.25 | 15 | 56.5 | 229965.2936 | 14245.6377 | 5.833%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 91081 | 225425.475 | 60 | 60 | 0 | 0.5 | 30 | 30 | 112712.7375 | 112712.7375 | 50%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 91081 | 93927.2812 | 30 | 38 | 0 | 0.5 | 5 | 5 | 15654.5469 | 78272.7344 | 83.33%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 2.7% | 5.5687 | 91081 | 507207.3187 | 60 | 23 | 37 | 0.25 | 15 | 52 | 439579.6763 | 67627.6425 | 13.33%
|  |  | D3020 - BOILERS | 2% | 4.125 | 91081 | 375709.125 | 60 | 60 | 0 | 0.25 | 15 | 15 | 93927.2812 | 281781.8438 | 75%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4% | 8.25 | 91081 | 751418.25 | 40 | 40.75 | 0 | 0.2125 | 5 | 5 | 93927.2812 | 657490.9688 | 87.5%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4% | 8.25 | 91081 | 751418.25 | 40 | 18.7833 | 21.2167 | 0.54333 | 21.7333 | 40 | 751418.25 | 0 | 0%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 2% | 4.125 | 91081 | 375709.125 | 40 | 0 | 40 | 0 | 0 | 40 | 375709.125 | 0 | 0%
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.5% | 3.0938 | 91081 | 281781.8438 | 20 | 20 | 0 | 0.1 | 2 | 2 | 28178.1844 | 253603.6594 | 90%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 91081 | 187854.5625 | 20 | 0 | 20 | 0 | 0 | 20 | 187854.5625 | 0 | 100%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 91081 | 37570.9125 | 20 | 17.75 | 2.25 | 0.625 | 12.5 | 14.75 | 27708.548 | 9862.3645 | 26.25%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 91081 | 244210.9312 | 60 | 53 | 7 | 0.25 | 15 | 22 | 89544.0081 | 154666.9231 | 63.33%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 91081 | 1314981.9375 | 30 | 16.45 | 13.55 | 0.65389 | 19.6167 | 30 | 1314981.9375 | 0 | 0%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 91081 | 563563.6875 | 20 | 17.0455 | 2.9545 | 0.56818 | 11.3636 | 14.3182 | 403460.3672 | 160103.3203 | 28.41%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 91081 | 56356.3688 | 20 | 12.6611 | 7.3389 | 0.62778 | 12.5556 | 19.8944 | 56058.9324 | 297.4364 | 0.5278%
|  |  | SUBTOTAL SERVICES | 34.5% | 71.1563 | 91081 | 6480982.4063
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 91081
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 91081
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 91081
|  |  | E1090 - OTHER EQUIPMENT |  |  | 91081
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 91081
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 91081
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 91081
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 91081
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 91081
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 91081 | 187854.5625 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 46963.6406 | 140890.9219 | 75%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 91081 | 93927.2812 | 30 | 0 | 30 | 0 | 0 | 30 | 93927.2812 | 0 | 0%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 91081 | 93927.2812 | 30 | 3.5 | 26.5 | 0.75 | 22.5 | 30 | 93927.2812 | 0 | 0%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 91081 | 93927.2812 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 23481.8203 | 70445.4609 | 75%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 91081 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 91081
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 91081 | 18785456.25 | [7 empty] | 4919239.8555 | 26.19%
100%

## Master File (Interior)
Avon Avenue (Brick-Avon Academy)
School Code: | 220
NPS Code: | 51
Street: | 219 Avon Avenue
City/Town: | Newark, NJ 07108
Database ID: | 26
Total size (gsf): | 91081
ROOM INFORMATION | [12 empty] | 53.7143 | Ave Condition | 0.50714 | [6 empty] | 18.9028 | Ave Condition | 0.30139 | [6 empty] | 8.3611 | Ave Condition | 0.56528 | [6 empty] | 26.4242 | Ave Condition | 0.50152 | [5 empty] | 23.4706 | Ave Condition | 0.47429 | [6 empty] | 51.7059 | Ave Condition | 0.50735 | [6 empty] | 27.85 | Ave Condition | 0.4 | [6 empty] | 22.5 | Ave Condition | 0.5 | [5 empty] | 25.375 | Ave Condition | 0.46875 | [5 empty] | Average Age | 30 | Ave Condition | 0.4 | [5 empty] | 23.8333 | Ave Condition | 0.54167 | [6 empty] | 7.5 | Ave Condition | 0.75 | [6 empty] | 11.85 | Ave Condition | 0.71167 | [6 empty] | 28.9833 | Ave Condition | 0.48333 | [6 empty] | 29.8667 | Ave Condition | 0.4 | [6 empty] | 7.7 | Ave Condition | 0.68667 | [6 empty] | 17.75 | Ave Condition | 0.625 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [6 empty] | 1.5 | Ave Condition | 0.9 | [5 empty] | Average Age | 10 | Ave Condition | 0.5 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Interior Door | [7 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [8 empty] | Plumbing Fixtures - Urinals | [7 empty] | Plumbing Fixtures - Showers | [8 empty] | Plumbing Fixtures - Drinking Fountains | [7 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
1 | UN-61 | Water Closet | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 26 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 0
2 | UN-62 | Custodial Closet | 1st Floor | A | Support |  |  | 44 | 12' | [9 empty] | Unfinished | [17 empty] | Plaster
3 | UN-63 | Faculty Water Closet | 1st Floor | A | Faculty Support |  |  | 33 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 2 | [7 empty] | 0
4 | UN-64 | Storage | 1st Floor | A | Support |  |  | 72 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5 | UN-65 | Storage | 1st Floor | A | Support |  |  | 89 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
6 | UN-66 | Storage | 1st Floor | A | Support |  |  | 122 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
7 | UN-67 | Stroage | 1st Floor | A | Support |  |  | 347 | N/A
8 | UN-68 | Cafetorium | 1st Floor | B | Food Service/Assembly (K-8) |  |  | 4877 | 16\' | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Metal Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [38 empty] | Full Recessed Stainless Steel Drinking Fountains | 30+ | 30 | Fair | 0.5 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present - Present - Present - Present - Present - Present - Present | Very old | [9 empty] | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | [19 empty] | Present | [98 empty] | Present - Present - Present - Present - Present - Present - Present | [26 empty] | Present
9 | UN-69 | Kitchen | 1st Floor | B | Food Service/Assembly (K-8) |  |  | 385 | N/A | CMU Back-up Wall | 31 | 45 | 38 | Fair | 0.5 |  |  |  | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Metal Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Tile | 31 | 45 | 38 | Fair | 0.5 |  |  |  | Stainless Steel Sinks | 30+ |  | 30 | Fair | 0.5 | 4 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 |  |  | Unit heater | [9 empty] | Dry Chemical | 30+ |  | 30 | Fair | 0.5 | [10 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present - Present - Present - Present | [26 empty] | Present - Present | [8 empty] | Present
10 | UN-70 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 102 | N/A
11 | UN-71 | Storage | 1st Floor | A | Food Service/Assembly (K-8) |  |  | 117 | N/A
12 | 201 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 795 | 10' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
13 | 202 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 705 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Very Good | 0.9 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Very Good | 0.9 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Poor | 0.25 | 0 |  | No power outlet connection | [6 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 1 |  | Wall mounted | [15 empty] | 3 | [71 empty] | 0 | Present
14 | 203 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 698 | 12' | [9 empty] | Wood | [17 empty] | Plaster
15 | 204 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 794 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Wood | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | Loose and sagging Ethernet cable | [6 empty] | 0 | [8 empty] | 0 | [17 empty] | 3 | [71 empty] | 0 | Present
16 | 205 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 768 | 12' | [9 empty] | Wood | [17 empty] | Acoustical Panel
17 | 206 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 768 | 12' | [9 empty] | Wood | [17 empty] | Acoustical Panel
18 | 207 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 822 | 12' | [9 empty] | Wood | [17 empty] | Acoustical Panel
19 | 208 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 822 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Wood | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Good | 0.75 | 0 |  | Water damage at perimeter ceiling | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  | Cast iron pipe | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 1 |  | Wall mounted | [15 empty] | 7 | [71 empty] | 0 | Present
20 | 209 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 768 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  | Cast iron pipe | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present - Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 9 | [71 empty] | 0 | Present
21 | 210 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 768 | 11' 8" | [9 empty] | Wood | [17 empty] | Plaster
22 | 211 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 706 | 12' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
23 | 212 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 723 | 12' 3" | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 41070 | 8 | Good | 0.75 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 9 | [71 empty] | 0 | Present
24 | 214 | Classroom | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 723 | 12' 3" | [9 empty] | Wood | [17 empty] | Plaster
25 | UN-72 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 119 | N/A
26 | UN-73 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 7 | N/A
27 | UN-74 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 32 | N/A
28 | UN-75 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 54 | N/A
29 | UN-76 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 190 | N/A
30 | UN-77 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 190 | N/A
31 | UN-78 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 54 | N/A
32 | UN-79 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 32 | N/A
33 | UN-80 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 7 | N/A
34 | UN-81 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 119 | N/A
35 | UN-82 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 178 | N/A
36 | UN-83 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 178 | N/A
37 | UN-84 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 97 | N/A
38 | UN-85 | Custodial Closet | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 22 | N/A
39 | UN-86 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 97 | N/A
40 | UN-87 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 22 | N/A
41 | UN-88 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 24 | N/A
42 | UN-89 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 95 | N/A
43 | UN-90 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 24 | N/A
44 | UN-91 | Storage | 2nd Floor | A | General Classroom (Grades 4-5) |  |  | 95 | N/A
45 | UN-92 | Girls\' Water Closet | 2nd Floor | A | Support |  |  | 172 | 9' 11" | Other (describe) | 60+ |  | 60 | Poor | 0.25 |  |  | Plaster on masonry | Ceramic Tile | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls with Wainscot | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Metal/Metal Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Tile | 31 | 45 | 38 | Fair | 0.5 |  |  | Tile and plaster wainscot | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 2 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 5 | [7 empty] | 0 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present - Present - Present - Present
46 | UN-93 | Custodial Closet | 2nd Floor | A | Support |  |  | 27 | 12' 3" | [9 empty] | Unfinished | [17 empty] | Plaster
47 | UN-94 | Water Closet | 2nd Floor | A | Administration |  |  | 51 | 12' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 2 | [7 empty] | 0
48 | UN-95 | N/A | 2nd Floor | A | Administration |  |  | 192 | 12' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
49 | UN-96 | Office | 2nd Floor | A | Administration |  |  | 209 | 12' 3" | [9 empty] | Wood | [17 empty] | Plaster
50 | UN-97 | N/A | 2nd Floor | A | Administration |  |  | 48 | N/A
51 | UN-98 | Vestibule | 2nd Floor | A | Administration |  |  | 175 | N/A | [9 empty] | Wood | [17 empty] | Plaster
52 | 301 | Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 750 | 10' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
53 | 304 | Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 750 | 10' 11" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
54 | 305 | Computer Lab | 3rd Floor | A | Technological Literacy |  |  | 963 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Metal/Metal Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  | Cast iron pipes | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Old fire detection | [6 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 31 | [71 empty] | 0 | Present
55 | 306 | Social Studies | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 963 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
56 | 307 | Science | 3rd Floor | A | Science (6-12) |  |  | 751 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Very Poor | 0.1 | 0 |  |  | Suspended Acoustical | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present | Very old | [6 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 4 | [71 empty] | 0 | Present
57 | 308 | Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 822 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
58 | 309 | Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 768 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
59 | 310 | Classroom | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 768 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
60 | 311 | 7th Grade Math | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 706 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
61 | 312 | 7th Grade Social Studies | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 723 | 12' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
62 | 313 | 8th Grade | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 723 | 12' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
63 | 314 | 8th Grade | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 723 | 12' 6" | Other (describe) | 60+ |  | 60 | Poor | 0.25 | 0 |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Very Poor | 0.1 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | very old | [6 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 1 |  | wall mounted | [15 empty] | 4 | [71 empty] | 0 | Present
64 | UN-99 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 119 | 12' | [9 empty] | Wood | [17 empty] | Plaster
65 | UN-100 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 19 | 10' 11" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
66 | UN-101 | Library | 3rd Floor | A | Media Center |  |  | 2077 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Carpet | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Metal/Metal Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 1 |  | Wall mounted | [15 empty] | 15 | [71 empty] | 0 | Present
67 | UN-102 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 17 | 10' 11" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
68 | UN-103 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 119 | 10' 10" | [9 empty] | Wood | [17 empty] | Plaster
69 | UN-104 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 97 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
70 | UN-105 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 22 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
71 | UN-106 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 97 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
72 | UN-107 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 22 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
73 | UN-108 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 170 | 13' 3" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 6 | [7 empty] | 0
74 | UN-109 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 24 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
75 | UN-110 | Storage | 3rd Floor | A | General Classroom (Grades 6-8) |  |  | 95 | 11' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
76 | UN-111 | N/A | 3rd Floor | A | Support |  |  | 17 | 7' 9" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
77 | UN-112 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 172 | 9' 11" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 4 | [7 empty] | 7
78 | UN-113 | Custodial Closet | 3rd Floor | A | Support |  |  | 27 | 12' 7" | [9 empty] | Unfinished | [17 empty] | Plaster
117 | UN-1 | Music | Ground Floor | A | Visual & Performing Arts |  |  | 598 | N/A | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Brick masonry | [52 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present | Paging phone
118 | UN-2 | N/A | Ground Floor | A | N/A |  |  | 153 | N/A
119 | UN-3 | N/A | Ground Floor | A | N/A |  |  | 153 | N/A
120 | UN-4 | Custodial Office | Ground Floor | A | Support |  |  | 850 | N/A
121 | UN-5 | Service | Ground Floor | A | Support |  |  | 398 | N/A
122 | UN-6 | Guidance Counselor | Ground Floor | A | Administration |  |  | 701 | 9' 7 | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Concrete | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 4 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | [28 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present
123 | UN-7 | N/A | Ground Floor | A | N/A |  |  | 250 | N/A
124 | UN-8 | N/A | Ground Floor | A | N/A |  |  | 105 | N/A
125 | UN-9 | N/A | Ground Floor | A | N/A |  |  | 151 | N/A
126 | UN-10 | Test Room | Ground Floor | A | General Classroom (Grades 1-3) | 20 | 32 | 431 | 10' 6" | [9 empty] | Vinyl Composition Tile (VCT)
127 | UN-11 | Boys\' Water Closet | Ground Floor | A | Support |  |  | 249 | N/A | Plaster on Metal Lath | 60+ |  | 60 | Poor | 0.25 |  |  |  | Ceramic Tile | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Ceramic tile wainscot | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Concrete | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 4 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Poor | 0.25 | 6 |  |  | Floor Unit | 30+ | 30 | Poor | 0.25 | 8 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  | Missing lens | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present
128 | UN-12 | Storage and Water Closet | Ground Floor | A | Support |  |  | 298 | 9' 7" | [9 empty] | Epoxy | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 0
129 | UN-13 | Girls' Water Closet | Ground Floor | A | Support |  |  | 249 | N/A | [59 empty] | 0 | [8 empty] | 0 | [7 empty] | 0
130 | UN-14 | Boiler Room | Ground Floor | A | Support |  |  | 2181 | N/A
131 | UN-15 | Machine | Ground Floor | A | Support |  |  | 382 | N/A
132 | UN-16 | Storage | Ground Floor | A | Support |  |  | 805 | 9' 6" | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Epoxy | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Brick masonry | [52 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [10 empty] | Present | [98 empty] | Present | Paging phone
133 | UN-17 | Vault | Ground Floor | A | Support |  |  | 267 | N/A
134 | UN-18 | Machine | Ground Floor | A | Support |  |  | 744 | 9' 6" | [9 empty] | Epoxy | [17 empty] | Plaster
135 | UN-19 | Storage | Ground Floor | A | Support |  |  | 1784 | 9' 6" | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Epoxy | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Brick masonry | [52 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 3 | [72 empty] | Present
136 | UN-20 | Storage | Ground Floor | A | General Classroom |  |  | 136 | 7' 6" | [9 empty] | Wood | [17 empty] | Plaster
137 | UN-21 | Storage | Ground Floor | A | General Classroom |  |  | 127 | 9' 7" | [9 empty] | Epoxy | [17 empty] | Plaster
138 | UN-22 | N/A | Ground Floor | A | N/A |  |  | 351 | N/A
139 | UN-23 | N/A | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 381 | N/A
140 | UN-24 | Gymnasium | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 4790 | 12' 9" | Brick, Exposed/Unfinished | 60+ |  | 60 | Poor | 0.25 |  |  |  | Other (describe) | 20+ |  | 20 | Poor | 0.25 |  |  | Rubber sports tile | Painted Walls | 41004 |  | 4.5 | Poor | 0.25 |  |  | Water damage and peeling paint on exterior wall | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Metal/Metal Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Poor | 0.25 |  |  | Plaster on brick | [52 empty] | Fluorescent Linear Pendant Mount Fixture | 0 | 7 | 3.5 | Very Good | 0.9 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present | Very old | [133 empty] | Present
141 | UN-25 | N/A | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 135 | N/A
142 | UN-26 | N/A | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 236 | N/A
143 | UN-27 | Custodial Closet | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 59 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
144 | UN-28 | Gymnasium/Multipurpose | Ground Floor | B | Phys. Ed. (Gym + Storage) |  |  | 5446 | 12' 9 | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  | Plaster | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 |  |  | Concealed spline | Metal/Metal Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 | [38 empty] | Full Recessed Stainless Steel Drinking Fountains | 30+ | 30 | Fair | 0.5 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Poor | 0.25 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Wet Chemical | 22 | 30 | 26 | Fair | 0.5 |  |  | Water | [7 empty] | Present - Present | [10 empty] | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 |  |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 6 | [72 empty] | Present
145 | UN-29 | Boys' Water Closet | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 281 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 0
146 | UN-30 | Gym Office | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 80 | 12' 9" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
147 | UN-31 | Staff Water Closet | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 49 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 0
148 | UN-32 | Storage | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 16 | N/A | [9 empty] | Epoxy | [17 empty] | Plaster
149 | UN-33 | Storage | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 436 | N/A
150 | UN-34 | Gym Office | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 83 | 8' 6" | [9 empty] | Epoxy | [17 empty] | Acoustical Panel
151 | UN-35 | Staff Water Closet | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 49 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 0
152 | UN-36 | Storage | Ground Floor | A | Phys. Ed. (Gym + Storage) |  |  | 17 | N/A | [9 empty] | Epoxy | [17 empty] | Plaster
153 | UN-37 | Girls\' Water Closet | Ground Floor | B | Phys. Ed. (Gym + Storage) |  |  | 281 | N/A | CMU Back-up Wall | 31 | 45 | 38 | Good | 0.75 |  |  | Plaster | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  | Peeling paint | Wood/Metal Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Concrete Block | 31 | 45 | 38 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 3 |  | 1 removed | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 4 | [7 empty] | 0 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present
154 | 101 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 755 | 12' 3" | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  | Cast iron pipe | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 3 | [71 empty] | 0 | Present
155 | 102 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 855 | 12~N 3 | [9 empty] | Wood | [17 empty] | Plaster
156 | 103 | Main Office | 1st Floor | A | Administration |  |  | 451 | 12' 3" | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Poor | 0.25 |  |  | No knob | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [55 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Window Mounted | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [10 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present
157 | 104 | Faculty Lounge | 1st Floor | A | Faculty Support |  |  | 750 | 12' 3" | [9 empty] | Wood | [17 empty] | Acoustical Panel
158 | 105 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 768 | 12' 3" | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | 0 |  | Cat iron pipe | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present | [7 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 3 | [71 empty] | 0 | Present
159 | 106 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 768 | 12' 3" | [9 empty] | Wood | [17 empty] | Plaster
160 | 107 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 727 | 12' 3" | [9 empty] | Wood | [17 empty] | Plaster
161 | 108 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 727 | 12' 3" | [9 empty] | Wood | [17 empty] | Plaster
162 | 109 | Teacher\'s Room | 1st Floor | A | Faculty Support |  |  | 648 | 12' 3" | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  | Masonry | In-Counter Lavatories | 30+ |  | 30 | Poor | 0.25 | [46 empty] | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | [19 empty] | Present - Present - Present - Present | [10 empty] | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | [11 empty] | IDF 1 | [106 empty] | Present
163 | 110 | Health Office | 1st Floor | A | Health Services |  |  | 238 | 12' 3" | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  | Peeling and water damage | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  | Masonry | [52 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present - Present - Present | [10 empty] | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9
164 | 111 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 647 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Demountable/Folding. | 16 | 30 | 23 | Poor | 0.25 | 0 |  | Masonry | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 |  | Drinking fountain | [43 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | 0 | [8 empty] | 0 | [8 empty] | 0 |  | No fire detection | [6 empty] | 0 |  |  | Wireless (WiFi) | 0 | 3 | 1.5 | Very Good | 0.9 | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 2 | [71 empty] | 0 | Present
165 | 112 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 689 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
192 | 113 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 723 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 41067 |  | 6.5 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  | Water damage at perimeter | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | Masonry | [6 empty] | 0 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [17 empty] | 2 | [71 empty] | 0 | Present
193 | 114 | Classroom | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 550 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
194 | UN-38 | Storage | 1st Floor | A | Faculty Support |  |  | 119 | N/A
195 | UN-39 | Principal\'s Office | 1st Floor | A | Administration |  |  | 293 | 12' 3" | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Good | 0.75 | [55 empty] | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Window Mounted | 16 | 21 | 18.5 | Fair | 0.5 | [19 empty] | Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [11 empty] | CCTV monitor | [97 empty] | Present - Present - Present - Present - Present - Present
196 | UN-40 | Water Closet | 1st Floor | A | Administration |  |  | 29 | N/A | [59 empty] | 1 | [8 empty] | 1 | [7 empty] | 0
197 | UN-41 | Water Closet | 1st Floor | A | Administration |  |  | 15 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [7 empty] | 0
198 | UN-42 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 119 | N/A
199 | UN-43 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 178 | N/A
200 | UN-44 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 178 | N/A
201 | UN-45 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 14 | N/A
202 | UN-46 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 14 | N/A
203 | UN-47 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 97 | N/A
204 | UN-48 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 22 | N/A
205 | UN-49 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 24 | N/A
206 | UN-50 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 95 | N/A
207 | UN-51 | Storage | 1st Floor | A | Health Services |  |  | 47 | N/A
208 | UN-52 | N/A | 1st Floor | A | Health Services |  |  | 47 | N/A
209 | UN-53 | N/A | 1st Floor | A | Health Services |  |  | 22 | N/A
210 | UN-54 | N/A | 1st Floor | A | Health Services |  |  | 393 | 12' 3" | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  | Masonry | Wall-Mounted Lavatories | 30+ |  | 30 | Good | 0.75 | 1 | [45 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Very Good | 0.9 |  |  |  | Toggle Wall Switches | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Very Good | 0.9 | [19 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present
211 | UN-55 | N/A | 1st Floor | A | Faculty Support |  |  | 59 | N/A
212 | UN-56 | N/A | 1st Floor | A | Faculty Support |  |  | 60 | N/A
213 | UN-57 | Boys\' Water Closet | 1st Floor | A | Support |  |  | 197 | 12' | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | Ceramic Tile | 20+ |  | 20 | Poor | 0.25 |  |  | Painted | Painted Walls with Wainscot | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 0 | 7 | 3.5 | Very Good | 0.9 |  |  |  | Wood/Wood Frame | 20+ | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 16 | 21 | 18.5 | Fair | 0.5 | 1 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 4 |  |  | Floor Unit | 30+ | 30 | Poor | 0.25 | 6 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Lay-In Fixture (Troffer) | 0 | 7 | 3.5 | Very Good | 0.9 |  |  |  | Toggle Wall Switches | 0 | 7 | 3.5 | Good | 0.75 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | [28 empty] | Present - Present - Present - Present - Present - Present - Present
214 | UN-58 | Girls' Water Closet | 1st Floor | A | Support |  |  | 197 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 8 | [7 empty] | 0
215 | UN-59 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 25 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
216 | UN-60 | Storage | 1st Floor | A | General Classroom (Grades 1-3) |  |  | 20 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
10519 | UN-114 | Electrical Room | Ground Floor | A | Support |  |  | 133
10520 | UN-115 | Strorage | Ground Floor | A | Support |  |  | 146
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [7 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [7 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
28 | A | Original 1905 | 1st Floor | [6 empty] | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Other (describe) | 20+ |  | 20 | Fair | 0.5 |  |  | Marble | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | [11 empty] | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on masonry | [9 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | [18 empty] | Present
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [7 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [7 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
94 | A | Original 1925 | 1st Floor | [6 empty] | Other (describe) | 20+ |  | 20 | Fair | 0.5 |  |  | Paint | Painted Walls | 0 | 3 | 1.5 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | [12 empty] | Other (describe) | 60+ | 60 | Good | 0.75 | [11 empty] | Plaster on masonry | [9 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 | [12 empty] | Wet Chemical | 41136 | 11.5 | Fair | 0.5 | [10 empty] | Present | [17 empty] | Present | [8 empty] | Present
95 | B | Original 1905 | 2nd Floor | [6 empty] | Other (describe) | 41070 |  | 8 | Fair | 0.5 |  |  | Paint | Painted Walls | 41004 |  | 4.5 | Poor | 0.25 |  |  |  | Suspended Acoustical | 16 | 21 | 18.5 | Fair | 0.5 | [12 empty] | Other (describe) | 60+ | 60 | Good | 0.75 |  |  | Plaster on masonry | Wall Mounted Stainless Steel Drinking Fountains | 41136 |  | 11.5 | Fair | 0.5 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 16 | 21 | 18.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wet Chemical | 41136 | 11.5 | Good | 0.75 | [10 empty] | Present | [17 empty] | Present | [8 empty] | Present
96 | C | Original 1905 | 3rd Floor | [6 empty] | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Poor | 0.25 |  |  |  | Suspended Acoustical | 22 | 30 | 26 | Poor | 0.25 | [12 empty] | Drywall (Gypsum)/Wood Stud Framing | 60+ | 60 | Fair | 0.5 | [21 empty] | Fluorescent Lay-In Fixture (Troffer) | 16 | 21 | 18.5 | Poor | 0.25 |  |  |  | Keyed Wall Switches | 30+ | 30 | Poor | 0.25 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Poor | 0.25 | [18 empty] | Present | [17 empty] | Present | [8 empty] | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Tread Finish | [7 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
92 | A | Original 1905 | Ground - 3rd Floor | [15 empty] | Reinforced Concrete | 30+ |  | 30 | Fair | 0.5 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Other (describe) | 0-7 | #VALUE! | Poor | 0.25 |  |  | Paint | Other (describe) | 0 | 7 | 3.5 | Poor | 0.25 |  |  | Paint | Metal/Metal Frame | 20+ |  | 20 | Poor | 0.25 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [19 empty] | Present
93 | B | Original 1925 | Ground - 3rd Floor | [6 empty] | Plaster on Metal Lath | 60+ |  | 60 | Good | 0.75 |  |  |  | Reinforced Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Other (describe) | 30+ | 30 | Poor | 0.25 |  |  | Painted concrete | Other (describe) | 30+ |  | 30 | Poor | 0.25 |  |  | Painted concrete | Metal/Metal Frame | [17 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 | 11.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [19 empty] | Present

## Master File (Systems)
systems | Question | Value1 |  | Average1 | Value2 |  | Average2 | systems | Question | Value1 |  | Average1 | Value2 | Average2
Systems | Seg ID | 736 |  |  | 740 |  |  | InfoTech | Seg ID | 283 |  |  | 285
| Bldg.Phase | A |  |  | B |  |  |  | Bldg.Phase | A |  |  | B
| Original | 1 |  |  | 0 |  |  |  | Original | 1 |  |  | 0
| Addition | 0 |  |  | 1 |  |  |  | Addition | 0 |  |  | 1
| Year Built | 1905/1925 |  |  | 1970 |  |  |  | Year Built | 1905/1925 |  |  | 1970
Domestic Water Heaters | Location | UN14 | [5 empty] | Entrance Facilities (Demarc or Cable Vault) | Location
| Description | Fuel/Fired Water Heater | [6 empty] | Description
| Age | 16 | 21 | 18.5 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | 3 Hot Water Storage Tanks / Copper Hot Water Piping | [6 empty] | Notes
Sanitary Drainage | Location | UN14 |  |  | Roof |  |  | Main Dist. Facility (MDF) | Location | Above Ground Level Floor
| Description | Sanitary Sewers |  |  | Other (describe) |  |  |  | Description | Cabinet and Rack
| Age | 60+ |  | 60 | 31 | 45 | 38 |  | Age | 41067 |  | 6.5
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes |  |  |  | Bathroom Vent Piping |  |  |  | Notes | Room 305
Building Support (other) Plumbing Systems | Location |  |  |  | Roof |  |  | MDF, HVAC Terminal Units | Location
| Description |  |  |  | Stormwater Area Drains |  |  |  | Description | Cast Iron Radiators
| Age |  |  |  | 31 | 45 | 38 |  | Age | 30+ |  | 30
| Condition |  |  |  | Fair |  | 0.5 |  | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fuel Piping | Location | UN14 | [5 empty] | MDF, Packaged Terminal Air Conditioner | Location
| Description | Gas Piping | [6 empty] | Description | Window Mounted
| Age | 60+ |  | 60 |  |  |  |  | Age | 41136 |  | 11.5
| Condition | Poor |  | 0.25 |  |  |  |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fuel Pumps | Location | [6 empty] | Inter. Data Facility (IDF #1) | Location | 109
| Description | [7 empty] | Description | Cabinet
| Age | [7 empty] | Age | 41067 |  | 6.5
| Condition | [7 empty] | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fuel Storage Tanks | Location | [6 empty] | IDF #1, HVAC Terminal Units | Location
| Description | [7 empty] | Description | Cast Iron Radiators
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fuel Fired Boilers | Location | UN14 | [5 empty] | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers | [6 empty] | Description | Window Mounted
| Age | 60+ |  | 60 |  |  |  |  | Age | 0 | 7 | 3.5
| Condition | Poor |  | 0.25 |  |  |  |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Condensate Return Package / Original / Poor Condition | [6 empty] | Notes
Furnaces | Location | [6 empty] | Inter. Data Facility (IDF #2) | Location |  |  |  | UN68
| Description | [7 empty] | Description |  |  |  | Wall/Mounted Cabinet
| Age | [7 empty] | Age |  |  |  | 41067 | 6.5
| Condition | [7 empty] | Condition |  |  |  | Good | 0.75
| CheckBox | [7 empty] | CheckBox |  |  |  | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Unit Ventilators | Location | [6 empty] | IDF #2, HVAC Terminal Units | Location
| Description | [7 empty] | Description |  |  |  | Other (describe)
| Age | [7 empty] | Age |  |  |  | 30+ | 30
| Condition | [7 empty] | Condition |  |  |  | Fair | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes |  |  |  | Supply Air Diffusers
Fan Coil Units | Location | [6 empty] | IDF #2, Packaged Terminal Air Conditioner | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Water Chillers | Location | [6 empty] | Inter. Data Facility (IDF #3) | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Cooling Towers | Location | [6 empty] | IDF #3, HVAC Terminal Units | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Packaged Terminal Air Conditioner | Location | [6 empty] | IDF #3, Packaged Terminal Air Conditioner | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Hydronic Piping System | Location | UN14 | [5 empty] | Inter. Data Facility (IDF #4) | Location
| Description | Zoned Hot Water System | [6 empty] | Description
| Age | 16 | 30 | 23 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Pumps | Location | UN14 | [5 empty] | IDF #4, HVAC Terminal Units | Location
| Description | Hydronic Pumps | [6 empty] | Description
| Age | 16 | 30 | 23 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Steam Piping System | Location | UN14 | [5 empty] | IDF #4, Packaged Terminal Air Conditioner | Location
| Description | Two Pipe | [6 empty] | Description
| Age | 60+ |  | 60 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
HVAC Air Distribution | Location | [6 empty] | Inter. Data Facility (IDF #5) | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Air Handling Units | Location | UN18 |  |  | UN33, UN71 |  |  | IDF #5, HVAC Terminal Units | Location
| Description | Indoor Air Handling Units (AHU) |  |  | Indoor Air Handling Units (AHU) |  |  |  | Description
| Age | 40+ |  | 40 | 40+ |  | 40 |  | Age
| Condition | Very Poor |  | 0.1 | Poor |  | 0.25 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | 1 |  |  | 3 |  |  |  | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Heating Only / Not Operable | [6 empty] | Notes
HVAC Fans | Location |  |  |  | Roof |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description |  |  |  | Other (describe) |  |  |  | Description
| Age |  |  |  | 40+ |  | 40 |  | Age
| Condition |  |  |  | Poor |  | 0.25 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes |  |  |  | Roof Exhaust Fans |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location | [6 empty] | Backbone Cable Dist. | Location
| Description | [7 empty] | Description
| Age |  |  | 20 |  |  |  |  | Age
| Condition |  |  | 0.1 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fire/Suppression (Standpipes), Water/Based | Location | [6 empty] | Horizontal Cable Dist. | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | UN14
| Description | Gas Engine Generators
| Age | 0 | 15 | 7.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
| Power Output | 44kva
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | UN6
| Description | D5010 120
| Age | 46 | 60 | 53
| Condition | Poor |  | 0.25
CheckBox
Quantity
| Voltage | 208V
Power Output
Elec Power
| Notes | 1200 Amps
Voice Communication Terminal Equipment | Location | UN2
| Description | PDX/Key Systems
| Age | 0 | 10 | 5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | 103
| Description | Public Address and Mass Notification Systems
| Age | 41233 |  | 10.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Clock Included
Video Surveillance Systems | Location | Entry Lobby #1
| Description | Analog Video Recording Devices
| Age | 41233 |  | 10.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | UN5
| Description | Fire Alarm Annunciation Panels
| Age | 40+ |  | 40
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Heat Detectors
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
| Description | Air Compressor (UN18)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Value2 |  | Average2 | Exterior | Question | Value1 |  | Average1
Exterior | Seg ID | 890 |  |  | 902 |  |  | SiteElements | Seg ID | 230
| Bldg.Phase | A |  |  | B |  |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  |  | Addition | 0
| Year Built | 1905/1925 |  |  | 1970 |  |  |  | Year Built | 1905/1925
(Foundation) Walls for Subgrade Enclosures, Primary | Location | [6 empty] | Roadways | Location
| Description | Brick, Solid (Mass) |  |  | Concrete, Cast/In/Place |  |  |  | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 | 31 | 45 | 38 |  | Age | 16 | 21 | 18.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location | [6 empty] | Parking Lots | Location
| Description | [7 empty] | Description | Asphalt (Bituminous)
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Poor |  | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Standard Slabs On Grade, Primary | Location | [6 empty] | Pedestrian Plazas and Walkways, Primary | Location
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place |  |  |  | Description
| Age | 60+ |  | 60 | 31 | 45 | 38 |  | Age
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | Grid
Standard Slabs On Grade, Secondary | Location | [6 empty] | Pedestrian Plazas and Walkways, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Floor Construction, Primary | Location | [6 empty] | Athletic, Recreational, and Playfield Areas, Primary | Location
| Description | Other (describe) |  |  | Steel Framing, w/ Steel Deck |  |  |  | Description | Other (describe)
| Age | 60+ |  | 60 | 31 | 45 | 38 |  | Age | 0 | 7 | 3.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | CIP concrete w/ clay tile infill | [6 empty] | Notes | Interlocking plastic surface: soccer field
Floor Construction, Secondary | Location | [6 empty] | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description | Other (describe) | [6 empty] | Description
| Age | 60+ |  | 60 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Reinforced concrete | [6 empty] | Notes
Roof Construction, Structural Frame, Primary | Location | [6 empty] | Site Lighting, Primary | Location
| Description | Wood, Heavy Timber |  |  | Steel Framing, w/ Steel Deck |  |  |  | Description | Pole Mounted H.I.D.
| Age | 60+ |  | 60 | 31 | 45 | 38 |  | Age | 41136 |  | 11.5
| Condition | Fair |  | 0.5 | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Wood trusses with wood deck | [6 empty] | Notes
Roof Construction, Structural Frame, Secondary | Location | [6 empty] | Site Lighting, Secondary | Location
| Description | [7 empty] | Description | Building Mounted H.I.D.
| Age | [7 empty] | Age | 22 | 30 | 26
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Exterior Walls / Exterior Assembly, Primary | Location | [6 empty] | Playground Surface | Location
| Description | Brick, Solid (Mass) |  |  | Brick, Solid (Mass) |  |  |  | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 | 31 | 45 | 38 |  | Age
| Condition | Poor |  | 0.25 | Fair |  | 0.5 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Exterior Walls / Exterior Assembly, Secondary | Location | [6 empty] | Playground Equipment | Location
| Description | [7 empty] | Description | B/Ball Backstops
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Poor |  | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Exterior Windows, Primary | Location | [6 empty] | TCUs | Location
| Description | Aluminum, Double Hung |  |  | Aluminum, Awning/Hopper |  |  |  | Description
| Age | 41136 |  | 11.5 | 30+ |  | 30 |  | Age
| Condition | Poor |  | 0.25 | Poor |  | 0.25 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Don't operate properly | [6 empty] | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated) |  |  | Glass, Single Pane
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Security Grilles |  |  | Screens, Insect / Security Grilles
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | Some missing and broken screens
Exterior Windows, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location
| Description | Fiber Reinforced Panel (FRP) |  |  | Fiber Reinforced Panel (FRP)
| Age | 0 | 15 | 7.5 | 0 | 15 | 7.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | Some are hard to close and open
Exterior Doors, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location
| Description | Asphalt Shingle |  |  | Polyurethane, Spray Applied
| Age | 0 | 7 | 3.5 | 0 | 7 | 3.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location
| Description |  |  |  | Aluminum
| Age |  |  |  | 30+ |  | 30
| Condition |  |  |  | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location
| Description | Copper |  |  | Other (describe)
| Age | 0 | 7 | 3.5 | 30+ |  | 30
| Condition | Fair |  | 0.5 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Mostly original with some replacements a year ago |  |  | Cast iron internal roof drain
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes