## FCI Summary
Building Name: | Miller Street School | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 79224
Number of Floors: | B + 4
School Age (years): | 100
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 33.5%
Facility Condition = | FAIR
FCI Deficiency Cost = | 5474340.5069
FCI Replacement Cost = | 16339950
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 557
Historic 2005 LRFP Capacity = | 553
Adjusted 2012 Capacity = | 563
Recent Occupancy % = | 98.93%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 81.83%
Classroom Adequacy = | FAIR
Special Spaces Adequacy % Score = | 37.55%
Special Spaces Adequacy = | VERY POOR

## Uniformat FCI
Building Name: |  | Miller Street School | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 79224
Largest Floor Level Area: |  | 21392
Vertical FAR Ratio: |  | 3.7034
School Age (years): |  | 100
Replacement Constr Cost/SF: |  | 275 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 206.25 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 1.8% | 3.7125 | 79224 | 294119.1 | 100 | 100 | 0 | 0.5 | 50 | 50 | 147059.55 | 147059.55 | 50%
|  |  | A1030 - SLAB ON GRADE | 1.5% | 3.0938 | 79224 | 245099.25 | 100 | 100 | 0 | 0.75 | 75 | 75 | 183824.4375 | 61274.8125 | 25%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.5375 | 79224 | 359478.9 | 100 | 100 | 0 | 0.5 | 50 | 50 | 179739.45 | 179739.45 | 50%
|  |  | SUBTOTAL SUBSTRUCTURE | 5.5% | 11.3438 | 79224 | 898697.25
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 22.6875 | 79224 | 1797394.5 | 100 | 100 | 0 | 0.75 | 75 | 75 | 1348045.875 | 449348.625 | 25%
|  |  | B1020 - ROOF CONSTRUCTION | 2.5% | 5.1562 | 79224 | 408498.75 | 100 | 100 | 0 | 0.5 | 50 | 50 | 204249.375 | 204249.375 | 50%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 9.5% | 19.5938 | 79224 | 1552295.25 | 100 | 100 | 0 | 0.39803 | 39.8026 | 39.8026 | 617854.3594 | 934440.8906 | 60.2%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 5.5% | 11.3438 | 79224 | 898697.25 | 30 | 24.25 | 5.75 | 0.625 | 18.75 | 24.5 | 733936.0875 | 164761.1625 | 18.33%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 2% | 4.125 | 79224 | 326799 | 30 | 22.3333 | 7.6667 | 0.75 | 22.5 | 30 | 326799 | 0 | 0%
|  |  | SUBTOTAL SHELL | 30.5% | 62.9063 | 79224 | 4983684.75
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 8.25 | 79224 | 653598 | 60 | 49.0286 | 10.9714 | 0.54054 | 32.4324 | 43.4039 | 472811.2791 | 180786.7209 | 27.66%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.0938 | 79224 | 245099.25 | 20 | 24.5694 | 0 | 0.53378 | 5 | 5 | 61274.8125 | 183824.4375 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 8.25 | 79224 | 653598 | 20 | 7.5 | 12.5 | 0.75 | 15 | 20 | 653598 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.0938 | 79224 | 245099.25 | 30 | 100 | 0 | 0.5 | 5 | 5 | 40849.875 | 204249.375 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 4% | 8.25 | 79224 | 653598 | 10 | 8.0278 | 1.9722 | 0.53846 | 5.3846 | 7.3568 | 480841.4346 | 172756.5654 | 26.43%
|  |  | C3020 - FLOOR FINISHES | 6% | 12.375 | 79224 | 980397 | 20 | 16.6622 | 3.3378 | 0.48077 | 9.6154 | 12.9532 | 634965.0217 | 345431.9783 | 35.23%
|  |  | C3030 - CEILING FINISHES | 6% | 12.375 | 79224 | 980397 | 30 | 30 | 0 | 0.52857 | 15.8571 | 15.8571 | 518209.8429 | 462187.1571 | 47.14%
|  |  | SUBTOTAL INTERIORS | 27% | 55.6875 | 79224 | 4411786.5
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 1% | 2.0625 | 79224 | 163399.5 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 163399.5 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.0938 | 79224 | 245099.25 | 60 | 22.5361 | 37.4639 | 0.59201 | 35.5208 | 60 | 245099.25 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.6812 | 79224 | 212419.35 | 60 | 18.5 | 41.5 | 0.25 | 15 | 56.5 | 200028.2213 | 12391.1288 | 5.833%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.475 | 79224 | 196079.4 | 60 | 60 | 0 | 0.5 | 30 | 30 | 98039.7 | 98039.7 | 50%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.0312 | 79224 | 81699.75 | 30 | 60 | 0 | 0.5 | 5 | 5 | 13616.625 | 68083.125 | 83.33%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 3.2% | 6.6 | 79224 | 522878.4 | 60 | 23 | 37 | 0.25 | 15 | 52 | 453161.28 | 69717.12 | 13.33%
|  |  | D3020 - BOILERS | 2.5% | 5.1562 | 79224 | 408498.75 | 60 | 38 | 22 | 0.25 | 15 | 37 | 251907.5625 | 156591.1875 | 38.33%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4.5% | 9.2812 | 79224 | 735297.75 | 40 | 28.8333 | 11.1667 | 0.33333 | 13.3333 | 24.5 | 450369.8719 | 284927.8781 | 38.75%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4.5% | 9.2812 | 79224 | 735297.75 | 40 | 19.6625 | 20.3375 | 0.25 | 10 | 30.3375 | 557677.3873 | 177620.3627 | 24.16%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 0% | 0 | 79224 | 0 | 40 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0%
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.5% | 3.0938 | 79224 | 245099.25 | 20 | 100 | 0 | 0 | 5 | 5 | 61274.8125 | 183824.4375 | 75%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.0625 | 79224 | 163399.5 | 20 | 100 | 0 | 0 | 5 | 5 | 40849.875 | 122549.625 | 75%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.4125 | 79224 | 32679.9 | 20 | 11.5 | 8.5 | 0.75 | 15 | 20 | 32679.9 | 0 | 0%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.6812 | 79224 | 212419.35 | 60 | 60 | 0 | 0.25 | 15 | 15 | 53104.8375 | 159314.5125 | 75%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 14.4375 | 79224 | 1143796.5 | 30 | 16.546 | 13.454 | 0.54885 | 16.4655 | 29.9195 | 1140728.8466 | 3067.6534 | 0.2682%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.1875 | 79224 | 490198.5 | 20 | 13.8679 | 6.1321 | 0.46607 | 9.3214 | 15.4536 | 378765.8767 | 111432.6233 | 22.73%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.61875 | 79224 | 49019.85 | 20 | 18.75 | 1.25 | 0.375 | 7.5 | 8.75 | 21446.1844 | 27573.6656 | 56.25%
|  |  | SUBTOTAL SERVICES | 34.5% | 71.1562 | 79224 | 5637282.75
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 79224
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 79224
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 79224
|  |  | E1090 - OTHER EQUIPMENT |  |  | 79224
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 79224
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 79224
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 79224
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 79224
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 79224
|  |  | G2020 - PARKING LOTS | 1% | 2.0625 | 79224 | 163399.5 | 30 | 30 | 0 | 0.25 | 7.5 | 7.5 | 40849.875 | 122549.625 | 75%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.0312 | 79224 | 81699.75 | 30 | 0 | 30 | 0 | 0 | 30 | 81699.75 | 0 | 0%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.0312 | 79224 | 81699.75 | 30 | 11.5 | 18.5 | 0.1 | 3 | 21.5 | 58551.4875 | 23148.2625 | 28.33%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.0312 | 79224 | 81699.75 | 30 | 11.5 | 18.5 | 0.75 | 22.5 | 30 | 81699.75 | 0 | 0%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 79224 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 79224
|  |  | REPLACEMENT COST PER SF |  | 206.25 | 79224 | 16339950 | [7 empty] | 5474340.5069 | 33.5%
100%
Note on J41: Tessier, Matthew: No Survey Data
Note on J42: Tessier, Matthew: No Survey Data
Note on J59: Tessier, Matthew: No Survey Data

## Master File (Interior)
Miller Street
School Code: | 530
NPS Code: | 82
Street: | 41 Miller St.
City/Town: | Newark,
Database ID: | 39
Total size (gsf): | 79225
ROOM INFORMATION | [12 empty] | 53.2222 | Ave Condition | 0.54605 | [6 empty] | 16.6622 | Ave Condition | 0.48077 | [6 empty] | 8.0278 | Ave Condition | 0.53846 | [5 empty] | 30 | Ave Condition | 0.52857 | [6 empty] | 24.5694 | Ave Condition | 0.53378 | [6 empty] | 49.0286 | Ave Condition | 0.54054 | [6 empty] | 24.6333 | Ave Condition | 0.57812 | [6 empty] | 14.125 | Ave Condition | 0.6875 | [6 empty] | 24.7 | Ave Condition | 0.52778 | [5 empty] | 30 | Ave Condition | 0.58333 | [6 empty] | 19.2222 | Ave Condition | 0.58333 | [6 empty] | 7.5 | Ave Condition | 0.75 | [5 empty] | 12.1379 | Ave Condition | 0.64655 | [5 empty] | 30 | Ave Condition | 0.5 | [5 empty] | 30 | Ave Condition | 0.25 | [6 empty] | 9.325 | Ave Condition | 0.25 | [5 empty] | 11.5 | Ave Condition | 0.75 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 8.575 | Ave Condition | 0.6625 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [8 empty] | Plumbing Fixtures - Urinals | [8 empty] | Plumbing Fixtures - Showers | [7 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [7 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [7 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [7 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [7 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
8594 | UN-1 | Custodial Closet | Basement | B | Support |  |  | 161 | N/A
8595 | UN-2 | Storage | Basement | A | Food Service/Assembly (K-8) |  |  | 22 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8596 | UN-3 | Storage | Basement | A | Food Service/Assembly (K-8) |  |  | 18 | N/A
8597 | UN-4 | Kitchen | Basement | B | Food Service/Assembly (K-8) |  |  | 519 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Poor | 0.25 |  |  | metal panel | Metal/Metal Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 3 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Poor | 0.25 |  |  | ducted air diffusers | [24 empty] | Present - Present | [133 empty] | Present - Present | [26 empty] | Present - Present | [8 empty] | Present
8598 | UN-5 | N/A | Basement | A | Food Service/Assembly (K-8) |  |  | 24 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8599 | UN-6 | Boys' Water Closet | Basement | A | Support |  |  | 146 | 9' 2" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 2 | [8 empty] | 2 | [8 empty] | 2
8600 | UN-7 | Girls' Water Closet | Basement | A | Support |  |  | 175 | 9' 8" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
8601 | UN-8 | Custodial Closet | Basement | A | Support |  |  | 86 | 9' 2" | [9 empty] | Unfinished | [17 empty] | Plaster
8602 | UN-9 | N/A | Basement | A | Support |  |  | 33 | 9' 2" | [9 empty] | Unfinished | [17 empty] | Plaster
8603 | UN-10 | N/A | Basement | B | N/A |  |  | 436 | N/A
8604 | UN-11 | N/A | Basement | A | N/A |  |  | 192 | N/A
8605 | UN-12 | Cafeteria | Basement | B | Food Service/Assembly (K-8) |  |  | 4190 | 10' | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 16 | 20 | 18 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ | 30 | Poor | 0.25 |  |  | concealed spline | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [9 empty] | 0 | [28 empty] | Wall Mounted Stainless Steel Drinking Fountains | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 30+ | 30 | Poor | 0.25 |  |  |  | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 |  |  | one toggle | Fin Tube Radiation | 30+ | 30 | Poor | 0.25 | [27 empty] | Present | [34 empty] | Present | [98 empty] | Present | [26 empty] | Present | [8 empty] | Present
8606 | 1 | Classroom | 1st Floor | A | General Classroom |  |  | 575 | 9' 5" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8607 | 2 | Classroom | 1st Floor | B | General Classroom |  |  | 596 | 9' 5" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  | water fountain head | [44 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Poor | 0.25 | 0 | [17 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 1 | [72 empty] | Present - Present - Present
8608 | 3 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 631 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8609 | 4 | Kindergarten Classroom | 1st Floor | A | Kindergarten Classroom |  |  | 631 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8610 | 103 | Classroom | 1st Floor | A | General Classroom |  |  | 787 | 11' 2" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 |  | Partial demountable partition with 104 | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | [47 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 16 | 21 | 18.5 | Poor | 0.25 | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 1 | [72 empty] | Present
8611 | 104 | Classroom | 1st Floor | A | General Classroom |  |  | 746 | 11' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8612 | 105 | Classroom | 1st Floor | A | General Classroom |  |  | 866 | 9' 0" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8613 | 106 | Classroom | 1st Floor | A | General Classroom |  |  | 618 | 8' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8614 | 107 | Classroom | 1st Floor | A | General Classroom |  |  | 821 | 8' 10" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Poor | 0.25 | 0 |  | ceiling mounted steam piping | Window Mounted | 0 | 7 | 3.5 |  |  | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 1 | [72 empty] | Present - Present
8615 | UN-13 | Main Office | 1st Floor | B | Administration |  |  | 510 | 9' 2" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ | 30 | Good | 0.75 |  |  | concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | [9 empty] | 0 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Poor | 0.25 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Poor | 0.25 | [18 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | [109 empty] | Present - Present - Present - Present | head end
8616 | UN-14 | Entry | 1st Floor | A | Administration |  |  | 66 | N/A
8617 | UN-15 | Office | 1st Floor | B | Administration |  |  | 181 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 |  |  | concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | [18 empty] | 0 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | [10 empty] | Present | [98 empty] | Present - Present - Present - Present - Present
8618 | UN-16 | Office | 1st Floor | A | Administration |  |  | 61 | N/A
8619 | UN-17 | Principal's Office | 1st Floor | B | Administration |  |  | 200 | N/A
8620 | UN-18 | N/A | 1st Floor | A | Administration |  |  | 27 | N/A
8621 | UN-19 | Women's Water Closet | 1st Floor | A | Administration |  |  | 18 | 7' 7" | [9 empty] | Epoxy | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8622 | UN-20 | Work Room | 1st Floor | A | Administration |  |  | 74 | N/A
8623 | UN-21 | Nurse | 1st Floor | B | Health Services |  |  | 244 | 7' 8" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Acoustical Panel | 30+ | 30 | Fair | 0.5 |  |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 16 | 21 | 18.5 | Fair | 0.5 | 1 | [8 empty] | 0 | [8 empty] | 0 | [28 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 22 | 30 | 26 | Fair | 0.5 | [18 empty] | Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | [109 empty] | Present - Present - Present - Present - Present - Present
8624 | UN-22 | Storage | 1st Floor | A | Health Services |  |  | 69 | 7 '8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8625 | UN-23 | Nurse's Water Closet | 1st Floor | A | Health Services |  |  | 25 | 7' 8" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8626 | UN-24 | N/A | 1st Floor | A | Health Services |  |  | 25 | N/A
8627 | UN-25 | N/A | 1st Floor | A | Health Services |  |  | 116 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8628 | UN-26 | Girls' Water Closet | 1st Floor | A | Support |  |  | 154 | 7' 7" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 2 | [8 empty] | 4 | [8 empty] | 0
8629 | UN-27 | Boys\' Water Closet | 1st Floor | B | Support |  |  | 169 | 7' 7" | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 |  |  |  | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Other (describe) | 30+ | 30 | Fair | 0.5 |  |  | Wood | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Tile | 16 | 30 | 23 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 16 | 21 | 18.5 | Good | 0.75 | 2 |  |  | Wall Hung Flush Valve | 16 | 21 | 18.5 | Good | 0.75 | 2 |  |  | Wall Hung | 16 | 21 | 18.5 | Good | 0.75 | 2 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Poor | 0.25 | [27 empty] | Present - Present - Present - Present - Present - Present - Present
8630 | UN-28 | Custodial Closet | 1st Floor | A | Support |  |  | 53 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
8631 | UN-29 | Boys' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 20 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8632 | UN-30 | Girls' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 20 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8633 | UN-31 | Boys' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 20 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8634 | UN-32 | Girls' Water Closet | 1st Floor | A | Kindergarten Classroom |  |  | 20 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8635 | UN-33 | Storage | 1st Floor | A | Support |  |  | 194 | 10' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8636 | UN-34 | Book Storage | 1st Floor | B | Support |  |  | 245 | 10' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
8637 | UN-35 | Custodial Closet | 1st Floor | A | Support |  |  | 27 | N/A
8638 | UN-36 | Custodial Water Closet | 1st Floor | A | Support |  |  | 29 | 11' 11" | [9 empty] | Epoxy | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8639 | UN-37 | N/A | 1st Floor | A | N/A |  |  | 9 | N/A
8640 | UN-38 | Storage | 1st Floor | A | Support |  |  | 143 | 7' 7" | [9 empty] | Epoxy | [17 empty] | Plaster
8641 | UN-39 | Custodial Lounge | 1st Floor | A | Support |  |  | 470 | 7' 7" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Epoxy | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [28 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | [18 empty] | Present - Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | [109 empty] | Present - Present - Present - Present - Present - Present - Present
8642 | UN-40 | Storage | 1st Floor | A | General Classroom |  |  | 44 | N/A
8643 | UN-41 | Girls' Water Closet | 1st Floor | A | General Classroom |  |  | 18 | 8' 2" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8644 | UN-42 | Boys' Water Closet | 1st Floor | A | General Classroom |  |  | 36 | 8' 2" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 1 | [8 empty] | 2 | [8 empty] | 0
8645 | UN-43 | Boiler Room | 1st Floor | A | Support |  |  | 2229 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
8646 | UN-44 | Storage | 1st Floor | A | Support |  |  | 1223 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
8647 | UN-45 | Custodial Closet | 1st Floor | A | Support |  |  | 23 | 8' 2" | [9 empty] | Unfinished | [17 empty] | Plaster
8648 | UN-46 | Pre-K Boys' and Girls' Water Closet | 1st Floor | A | Support |  |  | 239 | N/A | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 2 | [8 empty] | 4
8649 | 21 | Classroom | 2nd Floor | A | General Classroom |  |  | 676 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8650 | 22 | Classroom | 2nd Floor | A | General Classroom |  |  | 676 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8651 | 23 | Classroom | 2nd Floor | B | General Classroom |  |  | 677 | 9' 2" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 | [17 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 3 | [72 empty] | Present - Present - Present
8652 | 24 | Classroom | 2nd Floor | A | General Classroom |  |  | 676 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8653 | 25 | Classroom | 2nd Floor | A | General Classroom |  |  | 677 | N/A | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8654 | 26 | Classroom | 2nd Floor | B | General Classroom |  |  | 678 | 9' 2" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 | [17 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present - Present
8655 | 27 | Classroom | 2nd Floor | A | General Classroom |  |  | 678 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8656 | 28 | Classroom | 2nd Floor | A | General Classroom |  |  | 678 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8657 | 203 | Classroom | 2nd Floor | A | General Classroom |  |  | 817 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8658 | 204 | Classroom | 2nd Floor | A | General Classroom |  |  | 817 | 9' 2" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 3 | [72 empty] | Present
8659 | 205 | Classroom | 2nd Floor | A | General Classroom |  |  | 870 | 13' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8660 | 206 | Classroom | 2nd Floor | A | General Classroom |  |  | 825 | 13' 7" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8661 | 207 | Classroom | 2nd Floor | A | General Classroom |  |  | 821 | 13' 7" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Poor | 0.25 | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 1 | [72 empty] | Present - Present
8662 | UN-47 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 154 | 9' 2" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 2 | [8 empty] | 4 | [8 empty] | 0
8663 | UN-48 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 169 | 9' 2" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 2 | [8 empty] | 2 | [8 empty] | 4
8664 | UN-49 | Custodial Closet | 2nd Floor | B | Support |  |  | 53 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
8665 | UN-50 | Men\'s Water Closet | 2nd Floor | B | Faculty Support |  |  | 91 | 7' 11" | [8 empty] | N/A | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 |  |  | Concealed splines | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Tile | 16 | 30 | 23 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 16 | 21 | 18.5 | Fair | 0.5 | 1 |  |  | Wall Hung Flush Valve | 16 | 21 | 18.5 | Fair | 0.5 | 1 |  |  | Wall Hung | 16 | 21 | 18.5 | Fair | 0.5 | 1 | [19 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | [35 empty] | Present - Present - Present - Present - Present
8666 | UN-51 | Women's Water Closet | 2nd Floor | A | Faculty Support |  |  | 71 | 7' 11" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8667 | UN-52 | Teachers\' Lounge | 2nd Floor | B | Faculty Support |  |  | 245 | N/A | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 |  |  | Concealed splines | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 22 | 30 | 26 | Fair | 0.5 | 1 | [8 empty] | 0 | [8 empty] | 0 | [28 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 16 | 21 | 18.5 | Poor | 0.25 |  |  |  | Wet Chemical | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 |  |  | Water type | [7 empty] | Present - Present - Present - Present - Present - Present | [133 empty] | Present - Present - Present - Present - Present
8668 | UN-53 | Storage | 2nd Floor | A | Food Service/Assembly (K-8) |  |  | 408 | N/A | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ | 30 | Poor | 0.25 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present
8669 | UN-54 | Auditorium | 2nd Floor | A | Food Service/Assembly (K-8) |  |  | 3529 | 25' 3" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [46 empty] | Fluorescent Recessed Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 |  |  | 3 | Other (describe) | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 |  |  | water | [7 empty] | Present - Present - Present - Present - Present - Present - Present | [133 empty] | Present - Present - Present - Present - Present - Present
8670 | UN-55 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 260 | 9' 8" | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 5 | [8 empty] | 0
8671 | UN-56 | Storage | 2nd Floor | A | Support |  |  | 23 | 8' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
8672 | UN-57 | Custodial Closet | 2nd Floor | A | Support |  |  | 29 | 8' 1" | [9 empty] | Unfinished | [17 empty] | Plaster
8673 | 31 | Classroom | 3rd Floor | B | General Classroom |  |  | 676 | 9' 2" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 | [17 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 3 | [72 empty] | Present - Present - Present
8674 | 32 | Classroom | 3rd Floor | A | General Classroom |  |  | 676 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8675 | 33 | Classroom | 3rd Floor | A | General Classroom |  |  | 677 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8676 | 34 | Classroom | 3rd Floor | A | General Classroom |  |  | 676 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8677 | 35 | Computers | 3rd Floor | B | Technological Literacy |  |  | 677 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | 0 | [17 empty] | Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Fair | 0.5 | 0 | [17 empty] | 0 | [17 empty] | 25 | [72 empty] | Present - Present - Present - Present
8678 | 36 | Classroom | 3rd Floor | B | General Classroom |  |  | 678 | 9' 2" | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 | 0 |  |  | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | 0 | [17 empty] | Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Fair | 0.5 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 3 | [72 empty] | Present - Present - Present - Present - Present
8679 | 37 | Classroom | 3rd Floor | A | General Classroom |  |  | 678 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8680 | 38 | Classroom | 3rd Floor | A | General Classroom |  |  | 678 | 9' 2" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
8681 | 303 | Classroom | 3rd Floor | A | General Classroom |  |  | 817 | 13' 11" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8682 | 304 | Library | 3rd Floor | A | Media Center |  |  | 817 | 13' 11" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Carpet | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [46 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | [18 empty] | 0 | [8 empty] | 0 | [8 empty] | 6 | [72 empty] | Present
8683 | 305 | Classroom | 3rd Floor | A | General Classroom |  |  | 870 | 13' 11" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8684 | 306 | Classroom | 3rd Floor | A | General Classroom |  |  | 825 | 13' 10" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 |  |  | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 4 | [72 empty] | Present - Present
8685 | 307 | Classroom | 3rd Floor | A | General Classroom |  |  | 821 | 13' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8686 | UN-58 | Girls' Water Closet | 3rd Floor | B | Support |  |  | 154 | 9' 2" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 2 | [8 empty] | 4 | [8 empty] | 0
8687 | UN-59 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 169 | 9' 2" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 2 | [8 empty] | 2 | [8 empty] | 4
8688 | UN-60 | Custodial Closet | 3rd Floor | A | Support |  |  | 53 | N/A | [9 empty] | Unfinished | [17 empty] | Plaster
8689 | UN-61 | Men's Water Closet | 3rd Floor | A | Faculty Support |  |  | 91 | 7' 11" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 1
8690 | UN-62 | Women's Water Closet | 3rd Floor | A | Faculty Support |  |  | 71 | 7' 11" | [9 empty] | Ceramic Tile | [17 empty] | Acoustical Panel | [31 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
8691 | UN-63 | Vice Principal\'s Office | 3rd Floor | B | Administration |  |  | 245 | N/A | CMU Back-up Wall | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ | 30 | Fair | 0.5 |  |  | concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 46 | 60 | 53 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 | [46 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ | 30 | Fair | 0.5 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | [18 empty] | Present - Present - Present - Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | [109 empty] | Present - Present - Present - Present - Present - Present
8692 | UN-64 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 260 | 9' 2" | [9 empty] | Epoxy | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 2 | [8 empty] | 4
8693 | UN-65 | Storage | 3rd Floor | A | Support |  |  | 23 | 8' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
8694 | UN-66 | Custodial Closet | 3rd Floor | A | Support |  |  | 29 | 8' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
8695 | UN-67 | N/A | 3rd Floor | A | N/A |  |  | 11 | N/A
8696 | UN-68 | Storage | 3rd Floor | A | Support |  |  | 24 | 8' 1" | [27 empty] | Plaster
8697 | UN-69 | Balcony | 3rd Floor | A | Support |  |  | 698 | 12' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 41004 |  | 4.5 | Good | 0.75 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [28 empty] | Fluorescent Recessed Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [27 empty] | Present - Present - Present - Present - Present - Present - Present
8698 | 403 | Classroom | 4th Floor | A | General Classroom |  |  | 817 | 12' 10" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 4 | [72 empty] | Present
8699 | 404 | Classroom | 4th Floor | A | General Classroom |  |  | 817 | 12' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8700 | 405 | Classroom | 4th Floor | A | General Classroom |  |  | 866 | 12' 9" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 |  |  | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 4 | [72 empty] | Present - Present
8701 | 406 | Classroom | 4th Floor | A | General Classroom |  |  | 821 | 12' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
8702 | 407 | Classroom | 4th Floor | A | General Classroom |  |  | 821 | 12' 10" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Good | 0.75 | 0 |  |  | Painted Walls | 41004 |  | 4.5 | Fair | 0.5 | 0 |  |  | Plaster | 30+ | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 60+ |  | 60 | Fair | 0.5 | 0 | [8 empty] | 0 | [46 empty] | Fluorescent Linear Pendant Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ | 30 | Fair | 0.5 | 0 |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 |  |  | 0 | [5 empty] | Good | 0.75 | 0 | [9 empty] | Present - Present - Present | [18 empty] | Hardwired CAT 5/6 | 2012-07-10 |  | 1900-01-07 12:00 | Good | 0.75 | 0 | [17 empty] | 0 | [8 empty] | 0 | [8 empty] | 3 | [72 empty] | Present - Present - Present
8703 | UN-70 | Storage | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 47 | 9' 10" | [9 empty] | Wood | [17 empty] | Plaster
8704 | UN-71 | N/A | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 25 | N/A
8705 | UN-72 | Storage | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 92 | 9' 10" | [9 empty] | Wood | [17 empty] | Plaster
8706 | UN-73 | Storage | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 217 | 9' 10" | [9 empty] | Wood | [17 empty] | Plaster
8707 | UN-74 | Gymnasium | 4th Floor | A | Phys. Ed. (Gym + Storage) |  |  | 3376 | 17' 2" | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 41070 |  | 8 | Good | 0.75 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Good | 0.75 |  |  | Brick wainscot | Plaster | 30+ | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Metal Stud Framing | 60+ |  | 60 | Fair | 0.5 | [9 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [10 empty] | Wall Mounted Stainless Steel Drinking Fountains | 16 | 21 | 18.5 | Fair | 0.5 | [12 empty] | HID Surface Mount Fixture | 2012-08-15 | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ | 30 | Fair | 0.5 | [70 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [72 empty] | Present - Present - Present - Present
8708 | UN-75 | N/A | 4th Floor | A | N/A |  |  | 12 | N/A
8709 | UN-76 | Storage | 4th Floor | A | Support |  |  | 24 | 8' 1" | [27 empty] | Plaster
8710 | UN-77 | Girls' Water Closet | 4th Floor | A | Support |  |  | 260 | 9' 2" | [9 empty] | Epoxy | [17 empty] | Plaster | [31 empty] | 2 | [8 empty] | 2 | [8 empty] | 0
8711 | UN-78 | Storage | 4th Floor | A | Support |  |  | 24 | 8' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
8712 | UN-79 | Custodial Closet | 4th Floor | A | Support |  |  | 30 | 8' 4" | [9 empty] | Unfinished | [17 empty] | Plaster
8713 | UN-80 | Office | 4th Floor | A | Administration |  |  | 152 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [7 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
65 | A | Addition 1962 | 1st | [6 empty] | Brick, Exposed/Unfinished |  |  |  | Good | 0.75 |  |  |  | Solid Terrazzo |  |  |  | Good | 0.75 |  |  |  | Other (describe) |  |  |  | Good | 0.75 |  |  | Structural glazing tile | Plaster |  |  | Good | 0.75 |  |  | Acoustical | [9 empty] | Other (describe) |  |  |  | Good | 0.75 |  |  | Strucral glazing tile | [9 empty] | Incandescent Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | [5 empty] | Other (describe) | 30+ | 30 | Good | 0.75 |  |  | Ceiling diffuser | [16 empty] | Present | [15 empty] | Present
66 | B | Original 1912 | 1st | Emergency Exit | [5 empty] | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Poor | 0.25 |  |  |  | Other (describe) | 20+ |  | 20 | Fair | 0.5 |  |  | Painted concrete | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 |  |  | Marble | Plaster | 30+ | 30 | Good | 0.75 | [12 empty] | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on masonry | [9 empty] | Fluorescent Lay-In Fixture (Troffer) | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | [5 empty] | Cast Iron Radiators | 30+ | 30 | Poor | 0.25 | [19 empty] | Present | [15 empty] | Present
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [7 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [7 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [7 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
216 | A | Addition 1962 | Basement | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Fair | 0.5 |  |  |  | Acoustical Panel |  |  |  | Poor | 0.25 |  |  | Concealed spline | [8 empty] | Concrete Block | 60+ |  | 60 | Good | 0.75 | [21 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | [11 empty] | Wet Chemical | 2012-08-15 |  | 1900-01-10 12:00 | Fair | 0.5 | [10 empty] | Present
217 | B | Addition 1962 | 1st Floor | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 10+ |  | 10 | Good | 0.75 |  |  | Structural glazing tile | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 |  |  | Concealed spline | [8 empty] | Tile | 46 | 60 | 53 | Good | 0.75 |  |  |  | Wall Mounted Stainless Steel Drinking Fountains | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | [11 empty] | Wet Chemical | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | [10 empty] | Present | [23 empty] | Present
218 | C | Original 1912 | 2nd Floor | [6 empty] | Other (describe) | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | [11 empty] | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on masonry | Wall Mounted Stainless Steel Drinking Fountains | 16 | 21 | 18.5 | Fair | 0.5 |  |  | One does not work | [9 empty] | Fluorescent Lay-In Fixture (Troffer) | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | [12 empty] | Other (describe) | [6 empty] | Ceiling | Wet Chemical | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 | [10 empty] | Present | [15 empty] | Present | [7 empty] | Present
219 | D | Original 1912 + Addition 1962 | 3rd Floor | [6 empty] | Other (describe) | 20+ |  | 20 | Good | 0.75 |  |  | Paint | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  | Last 30' in addition see corridor 2 | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | [11 empty] | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on masonry | Wall Mounted Stainless Steel Drinking Fountains | 16 | 21 | 18.5 | Good | 0.75 | [12 empty] | Fluorescent Lay-In Fixture (Troffer) | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ | 30 | Good | 0.75 |  |  |  | Wet Chemical | 16 | 21 | 18.5 | Fair | 0.5 | [10 empty] | Present | [23 empty] | Present
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [7 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [7 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [7 empty] | Fire-Suppression (Sprinklers), Water-Based | [7 empty] | CCTV | [7 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
200 | A | Addition 1962 | Basement - 3rd | [6 empty] | Other (describe) |  |  |  | Good | 0.75 |  |  | Structural glazing tile | Reinforced Concrete |  |  |  | Good | 0.75 |  |  |  | Other (describe) |  |  |  | Good | 0.75 |  |  | Structural glazing tile | Plaster |  |  | Good | 0.75 |  |  |  | Terrazzo |  |  |  | Good | 0.75 |  |  |  | Terrazzo |  |  |  | Good | 0.75 |  |  |  | Metal/Metal Frame |  |  |  | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture |  |  |  | Good | 0.75 |  |  |  | Panel Breaker Switching |  |  | Good | 0.75 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Good | 0.75 | [18 empty] | Present
201 | B | Addition 1962 | Basement - 3rd | Condition of stairway towards the roof invert poor condition | [5 empty] | Drywall(Gypsum)/on CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Reinforced Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ | 30 | Fair | 0.5 |  |  | Water damage at top floor | Other (describe) | 2012-08-15 |  | 1900-01-10 12:00 | Poor | 0.25 |  |  | Paint | Other (describe) | 2012-08-15 |  | 1900-01-10 12:00 | Poor | 0.25 |  |  | Paint | Metal/Metal Frame | 2012-06-10 |  | 1900-01-07 | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Poor | 0.25 | [11 empty] | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [18 empty] | Present
202 | C | Addition 1962 | Basement - 3rd | [6 empty] | Other (describe) | 46 | 60 | 53 | Good | 0.75 |  |  | Structural facing tile | Reinforced Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Good | 0.75 |  |  | Structural facing tile | Other (describe) | 30+ | 30 | Good | 0.75 |  |  | Acoustical plaster | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  |  | Terrazzo | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 2012-08-15 |  | 1900-01-10 12:00 | Good | 0.75 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | [18 empty] | Present
203 | D | Original 1912 | 1st - 4th | [6 empty] | Brick, Exposed/Unfinished | 60+ |  | 60 | Good | 0.75 |  |  | on 2nd floor | Reinforced Concrete | 30+ |  | 30 | Good | 0.75 |  |  |  | Painted Walls | 0 | 3 | 1.5 | Good | 0.75 |  |  |  | Other (describe) | 30+ | 30 | Good | 0.75 |  |  | Painted concrete | Other (describe) | 30+ |  | 30 | Good | 0.75 |  |  |  | Other (describe) | 30+ |  | 30 | Good | 0.75 |  |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 |  |  |  | Panel Breaker Switching | 30+ | 30 | Fair | 0.5 | [27 empty] | Present
EXTERIORs INFORMATION

## Master File (Systems)
systems | Question | Value1 |  | Average1 | Value2 |  | Average2 | systems | Question | Value1 |  | Average1
Systems | Seg ID | 1100 |  |  | 1103 |  |  | InfoTech | Seg ID | 408
| Bldg.Phase | A |  |  | B |  |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  |  | Addition | 0
| Year Built | 1912 |  |  | 1962 |  |  |  | Year Built | 1912
Domestic Water Heaters | Location | UN43 | [5 empty] | Entrance Facilities (Demarc or Cable Vault) | Location
| Description | Fuel/Fired Water Heater | [6 empty] | Description
| Age | 16 | 21 | 18.5 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | 2 hot water storage tanks, copper piping | [6 empty] | Notes
Sanitary Drainage | Location | Roof |  |  | Roof |  |  | Main Dist. Facility (MDF) | Location | Above Ground Level Floor
| Description | Sanitary Drainage Piping Cleanouts |  |  | Other (describe) |  |  |  | Description | Floor mounted Rack style
| Age | 60+ |  | 60 | 60+ |  | 60 |  | Age | 41067 |  | 6.5
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Bathroom vent piping |  |  | Bathroom exhaust fan |  |  |  | Notes | 35
Building Support (other) Plumbing Systems | Location | Roof |  |  | Roof |  |  | MDF, HVAC Terminal Units | Location
| Description | Stormwater Area Drains |  |  | Stormwater Area Drains |  |  |  | Description | Cast Iron Radiators
| Age | 60+ |  | 60 | 60+ |  | 60 |  | Age | 30+ |  | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Internal roof areas drains |  |  | Internal roof area drains |  |  |  | Notes
Fuel Piping | Location | UN43 | [5 empty] | MDF, Packaged Terminal Air Conditioner | Location
| Description | Gas Piping | [6 empty] | Description | Window Mounted
| Age | 31 | 45 | 38 |  |  |  |  | Age | 41136 |  | 11.5
| Condition | Poor |  | 0.25 |  |  |  |  | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fuel Pumps | Location | [6 empty] | Inter. Data Facility (IDF #1) | Location | UN33
| Description | [7 empty] | Description | Wall mounted in cabinet
| Age | [7 empty] | Age | 41067 |  | 6.5
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fuel Storage Tanks | Location | [6 empty] | IDF #1, HVAC Terminal Units | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fuel Fired Boilers | Location | UN43 | [5 empty] | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers | [6 empty] | Description
| Age | 31 | 45 | 38 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Condensate return package poor condition | [6 empty] | Notes
Furnaces | Location | [6 empty] | Inter. Data Facility (IDF #2) | Location | 24
| Description | [7 empty] | Description | Wall mounted cabinet style
| Age | [7 empty] | Age | 41067 |  | 6.5
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Unit Ventilators | Location | [6 empty] | IDF #2, HVAC Terminal Units | Location
| Description | [7 empty] | Description | Fin Tube Radiation
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fan Coil Units | Location | [6 empty] | IDF #2, Packaged Terminal Air Conditioner | Location
| Description | [7 empty] | Description | Window Mounted
| Age | [7 empty] | Age | 41136 |  | 11.5
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Water Chillers | Location | [6 empty] | Inter. Data Facility (IDF #3) | Location | 202
| Description | [7 empty] | Description | Floor mounted cabinet style
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Cooling Towers | Location | [6 empty] | IDF #3, HVAC Terminal Units | Location
| Description | [7 empty] | Description | Fin Tube Radiation
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Packaged Terminal Air Conditioner | Location | [6 empty] | IDF #3, Packaged Terminal Air Conditioner | Location
| Description | [7 empty] | Description | Window Mounted
| Age | [7 empty] | Age | 16 | 21 | 18.5
| Condition | [7 empty] | Condition | Very Poor |  | 0.1
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Hydronic Piping System | Location | UN43 | [5 empty] | Inter. Data Facility (IDF #4) | Location | UN16 IDF0
| Description | Zoned Hot Water System | [6 empty] | Description | Wall mounted
| Age | 16 | 30 | 23 |  |  |  |  | Age | 41067 |  | 6.5
| Condition | Poor |  | 0.25 |  |  |  |  | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox | Secure
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Pumps | Location | UN43 | [5 empty] | IDF #4, HVAC Terminal Units | Location
| Description | Hydronic Pumps | [6 empty] | Description
| Age | 16 | 30 | 23 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Steam Piping System | Location | UN43 | [5 empty] | IDF #4, Packaged Terminal Air Conditioner | Location
| Description | Two Pipe | [6 empty] | Description
| Age | 31 | 45 | 38 |  |  |  |  | Age
| Condition | Poor |  | 0.25 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
HVAC Air Distribution | Location | [6 empty] | Inter. Data Facility (IDF #5) | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Air Handling Units | Location | [6 empty] | IDF #5, HVAC Terminal Units | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
HVAC Fans | Location | Roof |  |  | Roof |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  | Other (describe) |  |  |  | Description
| Age | 21 | 30 | 25.5 | 21 | 30 | 25.5 |  | Age
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Roof exhaust fan |  |  | Roof exhaust fan |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location | [6 empty] | Backbone Cable Dist. | Location | 35
| Description | [7 empty] | Description | Multimode Fiber Cable
| Age | [7 empty] | Age | 41067 |  | 6.5
| Condition | [7 empty] | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Fire/Suppression (Standpipes), Water/Based | Location | [6 empty] | Horizontal Cable Dist. | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | UN43
| Description | Gas Engine Generators
| Age | 0 | 15 | 7.5
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | UN43
| Description | D5010 120
| Age | 60+ |  | 60
| Condition | Poor |  | 0.25
CheckBox
Quantity
| Voltage | 208volts
Power Output
Elec Power
Notes
Voice Communication Terminal Equipment | Location | UN43
| Description | PDX/Key Systems
| Age | 21 | 30 | 25.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | UN13
| Description | Public Address and Mass Notification Systems
| Age | 0 | 10 | 5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Video Surveillance Systems | Location | Main lobby
| Description | Analog Video Recording Devices
| Age | 0 | 10 | 5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | UN43
| Description | Fire Alarm Annunciation Panels
| Age | 40+ |  | 40
| Condition | Very Poor |  | 0.1
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Exterior | Question | Value1 |  | Average1 | Value2 |  | Average2 | Exterior | Question | Value1 |  | Average1
Exterior | Seg ID | 2337 |  |  | 1456 |  |  | SiteElements | Seg ID | 341
| Bldg.Phase | A |  |  | B |  |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 |  |  |  | Original | 1
| Addition | 0 |  |  | 1 |  |  |  | Addition | 0
| Year Built | 1912 |  |  | 1962 |  |  |  | Year Built | 1912
(Foundation) Walls for Subgrade Enclosures, Primary | Location | typical a | [5 empty] | Roadways | Location | s/4
| Description | Brick, Solid (Mass) | [6 empty] | Description | Concrete
| Age | 60+ |  | 60 |  |  |  |  | Age | 30+ |  | 30
| Condition | Fair |  | 0.5 |  |  |  |  | Condition | Fair |  | 0.5
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location | [6 empty] | Parking Lots | Location | s/5
| Description | [7 empty] | Description | Asphalt (Bituminous)
| Age | [7 empty] | Age | 30+ |  | 30
| Condition | [7 empty] | Condition | Poor |  | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Standard Slabs On Grade, Primary | Location | typical a | [5 empty] | Pedestrian Plazas and Walkways, Primary | Location
| Description | Concrete, Cast/In/Place | [6 empty] | Description
| Age | 60+ |  | 60 |  |  |  |  | Age
| Condition | Good |  | 0.75 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Standard Slabs On Grade, Secondary | Location | [6 empty] | Pedestrian Plazas and Walkways, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Floor Construction, Primary | Location | typical a | [5 empty] | Athletic, Recreational, and Playfield Areas, Primary | Location
| Description | Other (describe) | [6 empty] | Description
| Age | 60+ |  | 60 |  |  |  |  | Age
| Condition | Good |  | 0.75 |  |  |  |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Cast in place beams and slab with clay tile infill | [6 empty] | Notes
Floor Construction, Secondary | Location | [6 empty] | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description | [7 empty] | Description
| Age | [7 empty] | Age
| Condition | [7 empty] | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Roof Construction, Structural Frame, Primary | Location | [6 empty] | Site Lighting, Primary | Location | typical
| Description | [7 empty] | Description | Pole Mounted H.I.D.
| Age | [7 empty] | Age | 41136 |  | 11.5
| Condition | [7 empty] | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Roof Construction, Structural Frame, Secondary | Location | [6 empty] | Site Lighting, Secondary | Location | typical
| Description | [7 empty] | Description | Building Mounted H.I.D.
| Age | [7 empty] | Age | 22 | 30 | 26
| Condition | [7 empty] | Condition | Poor |  | 0.25
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Exterior Walls / Exterior Assembly, Primary | Location | typical a |  |  | typical b |  |  | Playground Surface | Location | s/8
| Description | Brick, Solid (Mass) |  |  | Concrete, PC |  |  |  | Description | Rubberized
| Age | 60+ |  | 60 | 46 | 60 | 53 |  | Age | 41136 |  | 11.5
| Condition | Poor |  | 0.25 | Good |  | 0.75 |  | Condition | Very Poor |  | 0.1
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | Appears to need repointing. | [6 empty] | Notes
Exterior Walls / Exterior Assembly, Secondary | Location |  |  |  | typical b |  |  | Playground Equipment | Location | s/7
| Description |  |  |  | Brick, Solid (Mass) |  |  |  | Description | B/Ball Backstops
| Age |  |  |  | 46 | 60 | 53 |  | Age | 41136 |  | 11.5
| Condition |  |  |  | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes | 2 old ones in poor condition
Exterior Windows, Primary | Location | typical a |  |  | typical b |  |  | TCUs | Location
| Description | Aluminum, Double Hung |  |  | Aluminum, Double Hung |  |  |  | Description
| Age | 16 | 21 | 18.5 | 30+ |  | 30 |  | Age
| Condition | Good |  | 0.75 | Fair |  | 0.5 |  | Condition
| CheckBox | [7 empty] | CheckBox
| Quantity | [7 empty] | Quantity
| Voltage | [7 empty] | Voltage
| Power Output | [7 empty] | Power Output
| Elec Power | [7 empty] | Elec Power
| Notes | [7 empty] | Notes
Exterior Windows, Primary / Glazing | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Screens, Insect / Security Grilles
Quantity
Voltage
Power Output
Elec Power
| Notes | Screen on second floor: wood screens in very poor condition. Security grilles onfirst floor
Exterior Windows, Secondary | Location |  |  |  | first floor b
| Description |  |  |  | Aluminum, Awning/Hopper
| Age |  |  |  | 30+ |  | 30
| Condition |  |  |  | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Glazing | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
| CheckBox |  |  |  | Security Grilles
Quantity
Voltage
Power Output
Elec Power
| Notes |  |  |  | Basement windows
Exterior Doors, Primary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location | roof a |  |  | roof b
| Description | Asphalt, Built Up |  |  | Asphalt, Built Up
| Age | 16 | 21 | 18.5 | 16 | 21 | 18.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Some ponding and bubbling
Roofing, Secondary | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location | roof a |  |  | roof b
| Description | Aluminum |  |  | Aluminum
| Age | 16 | 21 | 18.5
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location | roof a |  |  | roof b
| Description | Other (describe) |  |  | Other (describe)
| Age | 30+ |  | 30
| Condition | Good |  | 0.75 | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Internal roof drains, cast iron |  |  | Internal roof drains, cast iron
Lightning Protection | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes