## FCI Summary
Building Name: | West Side High | 2012 LRFP CONDITION SUMMARY
Building Square Footage: | 145381
Number of Floors: | 3
School Age (years): | 86
FACILITY CONDITION
Facility Condition Index (FCI) Score = | 28.26%
Facility Condition = | FAIR
FCI Deficiency Cost = | 9242842.0572
FCI Replacement Cost = | 32710725
CAPACITY UTILIZATION
Recent 2012 Enrollment = | 756
Historic 2005 LRFP Capacity = | 554
Adjusted 2012 Capacity = | 711.5792
Recent Occupancy % = | 106.2%
EDUCATION ADEQUECY
Classroom Adequacy % Score = | 88.46%
Classroom Adequacy = | GOOD
Special Spaces Adequacy % Score = | 78.02%
Special Spaces Adequacy = | FAIR

## Uniformat FCI
Building Name: |  | West Side High | [13 empty] | FACILITY CONDITION INDEX (FCI) VALUE
Building Square Footage: |  | 145381
Largest Floor Level Area: |  | 69643
Vertical FAR Ratio: |  | 2.0875
School Age (years): |  | 86
Replacement Constr Cost/SF: |  | 300 | * Includes Sitework and Furnishings, Fixtures & Equipment
FCI Bldg Replace Cost/SF: |  | 225 | * Excludes Sitework and Furnishings, Fixtures & Equipment
UNIFORMAT FCI VALUE
|  |  |  | ELEMENT | 7 | QTY. | RPV | SL | AGE | BAL | CR | EL | RL | RSV | DEF | FCI
|  |  |  | % OF | COST | BLDG | VALUE | SERVICE | INSTALL | BALANCE | COND | EXTEND | REMAIN | RESID | DEFIC | %
| LEVEL 1 INFORMATION | LEVEL 2 INFORMATION | LEVEL 3 INFORMATION | TOTAL² | $ / S. F. | S. F. | $ | LIFE | LIFE | LIFE | RATING | LIFE | LIFE | VALUE | VALUE | SCORE
A | SUBSTRUCTURE | A10 - FOUNDATIONS | A1010 - STANDARD FOUNDATIONS | 1.8% | 4.05 | 145381 | 588793.05 | 100 | 86 | 14 | 0.5 | 50 | 64 | 376827.552 | 211965.498 | 36%
|  |  | A1030 - SLAB ON GRADE | 1.5% | 3.375 | 145381 | 490660.875 | 100 | 86 | 14 | 0.5 | 50 | 64 | 314022.96 | 176637.915 | 36%
|  | A20 - BASEMENT CONSTRUCTION | A2020 - BASEMENT WALLS | 2.2% | 4.95 | 145381 | 719635.95 | 100 | 86 | 14 | 0.5 | 50 | 64 | 460567.008 | 259068.942 | 36%
|  |  | SUBTOTAL SUBSTRUCTURE | 5.5% | 12.375 | 145381 | 1799089.875
B | SHELL | B10 - SUPERSTRUCTURE | B1010 - FLOOR CONSTRUCTION | 11% | 24.75 | 145381 | 3598179.75 | 100 | 86 | 14 | 0.5 | 50 | 64 | 2302835.04 | 1295344.71 | 36%
|  |  | B1020 - ROOF CONSTRUCTION | 2.5% | 5.625 | 145381 | 817768.125 | 100 | 86 | 14 | 0.625 | 62.5 | 76.5 | 625592.6156 | 192175.5094 | 23.5%
|  | B20 - EXTERIOR CLOSURE | B2010 - EXTERIOR WALLS | 9.5% | 21.375 | 145381 | 3107518.875 | 100 | 86 | 14 | 0.51862 | 51.8617 | 65.8617 | 2046664.825 | 1060854.05 | 34.14%
|  |  | B2020 - EXTERIOR WINDOWS & DOORS | 5.5% | 12.375 | 145381 | 1799089.875 | 30 | 23.3 | 6.7 | 0.45 | 13.5 | 20.2 | 1211387.1825 | 587702.6925 | 32.67%
|  | B30 - ROOFING | B3010 - ROOF COVERING & OPENINGS | 2% | 4.5 | 145381 | 654214.5 | 30 | 19.4167 | 10.5833 | 0.5 | 15 | 25.5833 | 557899.5875 | 96314.9125 | 14.72%
|  |  | SUBTOTAL SHELL | 30.5% | 68.625 | 145381 | 9976771.125
C | INTERIORS | C10 - INTERIOR CONSTRUCTION | C1010 - PARTITIONS | 4% | 9 | 145381 | 1308429 | 60 | 55.5 | 4.5 | 0.56579 | 33.9474 | 38.4474 | 838427.5303 | 470001.4697 | 35.92%
|  |  | C1020 - INTERIOR DOORS | 1.5% | 3.375 | 145381 | 490660.875 | 20 | 21.8182 | 0 | 0.49091 | 5 | 5 | 122665.2188 | 367995.6562 | 75%
|  |  | C1030 - FITTINGS / SPECIALTIES | 4% | 9 | 145381 | 1308429 | 20 | 12.6667 | 7.3333 | 0.70833 | 14.1667 | 20 | 1308429 | 0 | 0%
|  | C20 - STAIRCASES | C2010 - STAIR CONSTRUCTION | 1.5% | 3.375 | 145381 | 490660.875 | 30 | 86 | 0 | 0.5 | 5 | 5 | 81776.8125 | 408884.0625 | 83.33%
|  | C30 - INTERIOR FINISHES | C3010 - WALL FINISHES | 4% | 9 | 145381 | 1308429 | 10 | 10.4667 | 0 | 0.46167 | 5 | 5 | 654214.5 | 654214.5 | 50%
|  |  | C3020 - FLOOR FINISHES | 6% | 13.5 | 145381 | 1962643.5 | 20 | 18.675 | 1.325 | 0.52167 | 10.4333 | 11.7583 | 1153870.8244 | 808772.6756 | 41.21%
|  |  | C3030 - CEILING FINISHES | 6% | 13.5 | 145381 | 1962643.5 | 30 | 27.7368 | 2.2632 | 0.54825 | 16.4474 | 18.7105 | 1224069.7618 | 738573.7382 | 37.63%
|  |  | SUBTOTAL INTERIORS | 27% | 60.75 | 145381 | 8831895.75
D | SERVICES | D10 - CONVEYING SYSTEMS | D1010 - ELEVATORS & LIFTS | 0.7% | 1.575 | 145381 | 228975.075 | 60 | NONE | 0 | 0.1 | 0 | 0 | 0 | 228975.075 | 100%
|  | D20 - PLUMBING | D2010 - PLUMBING FIXTURES | 1.5% | 3.375 | 145381 | 490660.875 | 60 | 23.8972 | 36.1028 | 0.55927 | 33.5564 | 60 | 490660.875 | 0 | 0%
|  |  | D2020 - DOMESTIC WATER DISTRIBUTION | 1.3% | 2.925 | 145381 | 425239.425 | 60 | 3.5 | 56.5 | 0.75 | 45 | 60 | 425239.425 | 0 | 0%
|  |  | D2030 - SANITARY WASTE | 1.2% | 2.7 | 145381 | 392528.7 | 60 | 60 | 0 | 0.5 | 30 | 30 | 196264.35 | 196264.35 | 50%
|  |  | D2040 - RAIN WATER DRAINAGE | 0.5% | 1.125 | 145381 | 163553.625 | 30 | 60 | 0 | 0.25 | 5 | 5 | 27258.9375 | 136294.6875 | 83.33%
|  | D30 - HVAC | D3010 - ENERGY SUPPLY | 3.2% | 7.2 | 145381 | 1046743.2 | 60 | 7.5 | 52.5 | 0.5 | 30 | 60 | 1046743.2 | 0 | 0%
|  |  | D3020 - BOILERS | 2.5% | 5.625 | 145381 | 817768.125 | 60 | 7.5 | 52.5 | 0.5 | 30 | 60 | 817768.125 | 0 | 0%
|  |  | D3040 - DISTRIBUTION SYSTEMS | 4.5% | 10.125 | 145381 | 1471982.625 | 40 | 12.6667 | 27.3333 | 0.25 | 10 | 37.3333 | 1373850.45 | 98132.175 | 6.667%
|  |  | D3050 - TERMINAL AND PACKAGE UNITS | 4.5% | 10.125 | 145381 | 1471982.625 | 40 | 18.7317 | 21.2683 | 0.265 | 10.6 | 31.8683 | 1172738.9463 | 299243.6787 | 20.33%
|  |  | D3060 - HVAC CONTROLS & INSTRUMENTATION | 0% | 0 | 145381 | 0 | 40 | 0 | 40 | 0 | 0 | 40 | 0 | 0 | 0%
|  | D40 - FIRE PROTECTION | D4010 - FIRE PROTECTION SPRINKLER SYSTEM | 1.8% | 4.05 | 145381 | 588793.05 | 20 | 0 | 20 | 0 | 0 | 20 | 588793.05 | 0 | 0%
|  |  | D4020 - STAND-PIPE & HOSE SYSTEMS | 1% | 2.25 | 145381 | 327107.25 | 20 | 0 | 20 | 0 | 0 | 20 | 327107.25 | 0 | 0%
|  |  | D4030 - FIRE PROTECTION SPECIALTIES | 0.2% | 0.45 | 145381 | 65421.45 | 20 | 10.3158 | 9.6842 | 0.71053 | 14.2105 | 20 | 65421.45 | 0 | 0%
|  | D50 - ELECTRICAL | D5010 - ELECTRICAL SERVICE & DISTRIBUTION | 1.3% | 2.925 | 145381 | 425239.425 | 60 | 60 | 0 | 0.25 | 15 | 15 | 106309.8562 | 318929.5687 | 75%
|  |  | D5020 - LIGHTING & BRANCH WIRING | 7% | 15.75 | 145381 | 2289750.75 | 30 | 18.2862 | 11.7138 | 0.62736 | 18.8208 | 30 | 2289750.75 | 0 | 0%
|  |  | D5030 - COMMUNICATION & SECURITY | 3% | 6.75 | 145381 | 981321.75 | 20 | 11.3056 | 8.6944 | 0.66711 | 13.3423 | 20 | 981321.75 | 0 | 0%
|  |  | D5090 - OTHER ELECTRICAL SYSTEMS | 0.3% | 0.675 | 145381 | 98132.175 | 20 | 26.281 | 0 | 0.41167 | 5 | 5 | 24533.0438 | 73599.1313 | 75%
|  |  | SUBTOTAL SERVICES | 34.5% | 77.625 | 145381 | 11285200.125
E | EQUIPMENT & FURNISHINGS | E10 - EQUIPMENT | E1010 - COMMERCIAL EQUIPMENT |  |  | 145381
|  |  | E1020 - INSTITUTIONAL EQUIPMENT |  |  | 145381
|  |  | E1030 - VEHICULAR EQUIPMENT |  |  | 145381
|  |  | E1090 - OTHER EQUIPMENT |  |  | 145381
|  | E20 - FURNISHINGS | E2010 - FIXED FURNISHINGS |  |  | 145381
|  |  | E2020 - MOVABLE FURNISHINGS |  |  | 145381
|  |  | SUBTOTAL EQUIPMENT & FURNISHINGS | 0% |  | 145381
F | SPECIAL CONSTRUCTION | F10 - SPECIAL CONSTRUCTION | F1010 - SPECIAL STRUCTURES |  |  | 145381
|  |  | SUBTOTAL SPECIAL CONST. & DEMO | 0% |  | 145381
|  |  | G2020 - PARKING LOTS | 1% | 2.25 | 145381 | 327107.25 | 30 | 26 | 4 | 0.25 | 7.5 | 11.5 | 125391.1125 | 201716.1375 | 61.67%
|  |  | G3030 - PEDESTRIAN PAVING | 0.5% | 1.125 | 145381 | 163553.625 | 30 | 26 | 4 | 0.25 | 7.5 | 11.5 | 62695.5563 | 100858.0688 | 61.67%
|  |  | G2040 - PLAYGROUND SURFACE | 0.5% | 1.125 | 145381 | 163553.625 | 30 | 30 | 0 | 0.175 | 5.25 | 5.25 | 28621.8844 | 134931.7406 | 82.5%
|  |  | G2040 - PLAYGROUND EQUIPMENT | 0.5% | 1.125 | 145381 | 163553.625 | 30 | 26 | 4 | 0.1 | 3 | 7 | 38162.5125 | 125391.1125 | 76.67%
|  |  | G2050 - LANDSCAPING | 0% | 0 | 145381 | 0
|  |  | SUBTOTAL BUILDING SITE WORK | 2.5% |  | 145381
|  |  | REPLACEMENT COST PER SF |  | 225 | 145381 | 32710725 | [7 empty] | 9242842.0572 | 28.26%
100%
Note on J41: Tessier, Matthew: No Survey Data
Note on J42: Tessier, Matthew: No Survey Data

## Master File (Interior)
West Side High | [82 empty] | ü
School Code: | 80
NPS Code: | 034/029
Street: | 403 S. Orange Ave.
City/Town: | Newark, NJ 07103
Database ID: | 80
Total size (gsf): | 145501
ROOM INFORMATION | [11 empty] | Average Age | 55.2979 | Ave Condition | 0.53723 | [5 empty] | Average Age | 18.675 | Ave Condition | 0.52167 | [5 empty] | Average Age | 10.4667 | Ave Condition | 0.46167 | [5 empty] | Average Age | 27.7368 | Ave Condition | 0.54825 | [5 empty] | Average Age | 21.8182 | Ave Condition | 0.49091 | [5 empty] | Average Age | 55.5 | Ave Condition | 0.56579 | [5 empty] | Average Age | 21 | Ave Condition | 0.56944 | [5 empty] | Average Age | 21.875 | Ave Condition | 0.57692 | [5 empty] | Average Age | 25.4444 | Ave Condition | 0.55 | [5 empty] | Average Age | 28.6667 | Ave Condition | 0.5 | [5 empty] | Average Age | 22.5 | Ave Condition | 0.6 | [5 empty] | Average Age | 12.6667 | Ave Condition | 0.70833 | [5 empty] | Average Age | 13.3585 | Ave Condition | 0.63208 | [5 empty] | Average Age | 29.8431 | Ave Condition | 0.485 | [5 empty] | Average Age | 29.7551 | Ave Condition | 0.28 | [5 empty] | Average Age | 7.7083 | Ave Condition | 0.25 | [5 empty] | Average Age | 10.3158 | Ave Condition | 0.71053 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | 10 | Ave Condition | 0.50806 | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0! | [5 empty] | Average Age | #DIV/0! | Ave Condition | #DIV/0!
[10 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Interior Door | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Lavatories | [8 empty] | Plumbing Fixtures - Toilets | [8 empty] | Plumbing Fixtures - Urinals | [8 empty] | Plumbing Fixtures - Showers | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Toilet Partitions | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Package Terminal Air Conditioner | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | Wifi | [8 empty] | Ethernet | [8 empty] | CCTV | [8 empty] | Smartboard | [8 empty] | Projectors | [8 empty] | CPUs | [8 empty] | Fumehood | [8 empty] | Compressed Air | [8 empty] | Gas | [8 empty] | Eyewash Station | [8 empty] | Fixed Lab Stations | [8 empty] | Branch Wiring | [8 empty] | Comm/Security | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Fittings | [8 empty] | HVAC Controls/Instrumentation | [8 empty] | Warming Station | [8 empty] | Full Service Kitchen
RoomID | Number | Room Name | Level | Phase | Use | Length | Width | Area | Height | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes | Description | Age |  |  | Condition |  | Quantity | Checkbox | Notes
FORMULA BAR
4862 | 105 | Classroom | 1st Floor | A | General Classroom (Grades 9-12) |  |  | 761 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 0 | 5 | 2.5 | Fair | 0.5 | 0 |  | Cracks | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 41136 |  | 11.5 | Poor | 0.25 | 0 |  | Missing tiles, water damage | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | With back wall in gyp board | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 | 0 | [11 empty] | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 | [72 empty] | Present
4863 | 107 | Home Economics | 1st Floor | A | Technological Literacy |  |  | 799 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 |  | With gyp board for shorter partitions | Wall-Mounted Lavatories | 41136 |  | 11.5 | Good | 0.75 | 1 | [47 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.5 | 0 |  | Supply grill on the walls | [9 empty] | Wet Chemical | 41136 |  | 11.5 | Good | 0.75 |  |  | Water type | [7 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 2 | [72 empty] | Present - Present
4864 | 108 | Classroom | 1st Floor | A | General Classroom (Grades 9-12) |  |  | 919 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4865 | 110 | Classroom | 1st Floor | A | General Classroom (Grades 9-12) |  |  | 669 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4866 | 110 | Classroom | 1st Floor | A | General Classroom (Grades 9-12) |  |  | 753 | 11'
4867 | 111 | Classroom | 1st Floor | A | General Classroom (Grades 9-12) |  |  | 658 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4868 | 112 | Classroom | 1st Floor | A | General Classroom (Grades 9-12) |  |  | 679 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on cmu | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | [44 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 6 | [72 empty] | Present
4869 | 113 | Music | 1st Floor | A | Visual & Performing Arts |  |  | 665 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on cmu | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | [12 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [30 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 6 CPUs | [7 empty] | Present | B. | [97 empty] | Present - Present
4870 | 114 | Classroom | 1st Floor | A | General Classroom (Grades 9-12) |  |  | 759 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4871 | 115 | Special Needs Services | 1st Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 373 | 10' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 16 | 20 | 18 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 | 0 |  | Plaster on cmu | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Dry Chemical | 16 | 21 | 18.5 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [98 empty] | 0
4872 | UN-1 | Classroom | 1st Floor | A | General Classroom |  |  | 316 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4873 | UN-2 | Custodians\' Office | 1st Floor | A | Administration |  |  | 217 | 11' 10" | Plaster on Metal Lath | 60+ |  | 60 | Good | 0.75 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Good | 0.75 |  |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on cmu | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Poor | 0.25 | [19 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 1 CPU | [106 empty] | Present - Present - Present - Present - Present - Present
4874 | UN-3 | Water Closet | 1st Floor | A | Administration |  |  | 39 | 11' | [9 empty] | Epoxy | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Good | 0.75 | 1 | [8 empty] | 0 | [20 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 | [35 empty] | 0 | Present - Present - Present - Present - Present - Present
4875 | UN-4 | Storage | 1st Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 30 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4876 | UN-5 | Storage | 1st Floor | A | Self-Contained Sp. Ed. Classroom |  |  | 46 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4877 | UN-6 | Athletic Office | 1st Floor | A | Administration |  |  | 288 | 9' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4878 | UN-7 | Conference Room | 1st Floor | A | Faculty Support |  |  | 730 | 11' | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Carpet | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Brick | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 |  |  |  | Window Mounted | 41136 |  | 11.5 | Poor | 0.25 | [19 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Good | 0.75 |  |  | 4 computers | [106 empty] | Present - Present - Present
4879 | UN-8 | Capital One Bank | 1st Floor | A | Technological Literacy |  |  | 700 | 11' | [9 empty] | Carpet | [17 empty] | Plaster
4880 | UN-9 | Vice Principal\'s Office | 1st Floor | A | Administration |  |  | 156 | 11' | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Brick | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Poor | 0.25 | [19 empty] | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [11 empty] | 1 desktop | [97 empty] | Present - Present - Present - Present
4881 | UN-10 | Storage | 1st Floor | A | Administration |  |  | 20 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4882 | UN-11 | Faculty Lounge | 1st Floor | A | Administration |  |  | 51 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4883 | UN-12 | Safe | 1st Floor | A | Administration |  |  | 51 | 12' | [9 empty] | Unfinished | [17 empty] | Plaster
4884 | UN-13 | Principal's Office | 1st Floor | A | Administration |  |  | 296 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4885 | UN-14 | Main Office | 1st Floor | A | Administration |  |  | 650 | 10' | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 | 0 |  | 2x4 | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Brick | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Poor | 0.25 | 0 |  |  | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [9 empty] | 0 | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [107 empty] | 0 | Present - Present
4886 | UN-15 | Vice Principal\'s Office | 1st Floor | A | Administration |  |  | 292 | N/A
4887 | UN-16 | CST | 1st Floor | A | Administration |  |  | 253 | N/A
4888 | UN-17 | Faculty Room | 1st Floor | A | Faculty Support |  |  | 400 | 10' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Plaster/Wood Stud Framing | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wall-Mounted Lavatories | 41136 |  | 11.5 | Fair | 0.5 | [48 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Poor | 0.25 |  |  |  | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present
4889 | UN-18 | Storage | 1st Floor | A | Faculty Support |  |  | 30 | 11' | [9 empty] | Unfinished | [17 empty] | Plaster
4890 | UN-19 | Faculty Water Closet | 1st Floor | A | Faculty Support |  |  | 42 | 9' | [8 empty] | N/A | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 16 | 21 | 18.5 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Tile | 16 | 30 | 23 | Fair | 0.5 | [9 empty] | 0 |  |  | Floor Mounted Flush Valve | 22 | 30 | 26 | Fair | 0.5 | 1 | [8 empty] | 0 | [20 empty] | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 |  |  |  | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | [37 empty] | Present - Present - Present - Present | Strobe
4891 | UN-20 | Storage | 1st Floor | A | Administration |  |  | 40 | 11' | [9 empty] | Unfinished | [17 empty] | Plaster
4892 | UN-21 | Attendance Office | 1st Floor | A | Administration |  |  | 181 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4893 | UN-22 | Storage | 1st Floor | A | Support |  |  | 99 | 11' | [9 empty] | Unfinished | [17 empty] | Plaster
4894 | UN-23 | Office | 1st Floor | A | Administration |  |  | 283 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 41070 |  | 8 | Fair | 0.5 |  |  | Repair | Painted Walls | 10+ |  | 10 | Fair | 0.5 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster metal lath, plaster on CMU, gypboard on metal stud | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | [11 empty] | W/duct work supply diffusers | [16 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [109 empty] | Present - Present - Present - Present
4895 | UN-24 | Custodial Closet | 1st Floor | A | Support |  |  | 40 | 11' 10 | [9 empty] | Unfinished | [17 empty] | Plaster
4896 | UN-25 | Custodial Closet | 1st Floor | A | Faculty Support |  |  | 41 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
4897 | UN-26 | Storage | 1st Floor | A | Support |  |  | 37 | 11' 10" | [9 empty] | Unfinished | [17 empty] | Plaster
4898 | UN-27 | Boiler Room | 1st Floor | A | Support |  |  | 209 | N/A
4899 | UN-28 | Security Office | 1st Floor | A | Administration |  |  | 333 | 11' | Brick, Exposed/Unfinished | 60+ |  | 60 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 | 0 |  | Brick | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Ventilators | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  |  | Dry Chemical | 30+ |  | 30 | Good | 0.75 | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 CPU | [6 empty] | 0 | [98 empty] | 0
4900 | UN-29 | Storage | 1st Floor | A | Support |  |  | 841 | 11' | [9 empty] | Unfinished | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
4901 | UN-30 | Computer Room | 1st Floor | A | Technological Literacy |  |  | 1072 | 10' | [9 empty] | Carpet | [17 empty] | Acoustical Panel
4902 | UN-31 | Computer Room | 1st Floor | A | Technological Literacy |  |  | 1072 | 10' | [6 empty] | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Metal/Metal Frame | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Drywall (Gypsum)/Metal Stud Framing | 60+ |  | 60 | Good | 0.75 | 0 |  | Plaster on cmu | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Other (describe) | 30+ |  | 30 | Good | 0.75 | 0 |  | Ceiling diffusers | [9 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 | [17 empty] | 27 | [71 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4903 | UN-32 | Weight Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 1307 | 11' | Brick, Exposed/Unfinished | 60+ |  | 60 | Good | 0.75 | 0 |  |  | Other (describe) | 16 | 20 | 18 | Good | 0.75 | 0 |  | Rubber (interlocking) | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Other (describe) | 60+ |  | 60 | Poor | 0.25 | 0 |  | Brick | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 |  |  | 0 |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 | 0 |  | Ceiling diffusers | [24 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4904 | UN-33 | Training Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 546 | 11' | [9 empty] | Other (describe) | [7 empty] | Rubber | [9 empty] | Acoustical Panel
4905 | UN-34 | Locker Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 747 | 11' | [9 empty] | Unfinished | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 | 0 |  | Brick | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | 0 |  | And exposed duct exhaust | [24 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4906 | UN-35 | Storage | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 478 | 11' | [9 empty] | Unfinished | [17 empty] | Acoustical Panel
4907 | UN-36 | Office | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 223 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4908 | UN-37 | Water Closet | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 130 | 11' | [9 empty] | Ceramic Tile | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Very Poor | 0.1 |  |  |  | Other (describe) | 30+ |  | 30 | Good | 0.75 |  |  | Painted exposed concrete | [9 empty] | Other (describe) | 60+ |  | 60 | Poor | 0.25 |  |  | Plaster on cmu | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 1 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Poor | 0.25 | 1 |  |  | Floor Unit | 30+ |  | 30 | Fair | 0.5 | 2 | [29 empty] | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 |  |  | Toilet exhaust | [25 empty] | Present - Present - Present - Present - Present - Present - Present
4909 | UN-38 | Showers | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 189 | 11' | [9 empty] | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Unfinished Walls | 10+ |  | 10 | Fair | 0.5 |  |  | Brick and tile | Plaster | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Brick | [27 empty] | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Gang shower | [18 empty] | Incandescent Pendant Mount Fixture | 30+ |  | 30 | Poor | 0.25 |  |  | With compact fluorescent lamp | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 |  |  | And toilet exhaust | [25 empty] | Present - Present - Present - Present - Present - Present - Present
4910 | UN-39 | Storage | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 80 | 11' | [9 empty] | Unfinished | [17 empty] | Plaster
4911 | UN-40 | Auditorium | 1st Floor | A | Assembly/Large Group (9-12) |  |  | 6028 | N/A | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on wood panelling | Wood | 20+ |  | 20 | Good | 0.75 | 0 |  | Painted | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  | Wood wainscot | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  | Ornamental | Wood/Wood Frame | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 | 0 |  | Plaster on cmu | [54 empty] | Incandescent Pendant Mount Fixture | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [11 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [133 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4912 | UN-41 | Boys\' Water Closet | 1st Floor | A | Support |  |  | 602 | 8' | Other (describe) | 60+ |  | 60 | Poor | 0.25 | 0 |  | Ceramic tile on metal lath | Epoxy | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Ceramic Tile Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Tile | 60+ |  | 60 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 30+ |  | 30 | Poor | 0.25 | 4 |  | Was 5, but missing one | Wall Hung Flush Valve | 30+ |  | 30 | Fair | 0.5 | 7 |  |  | Floor Unit | 30+ |  | 30 | Fair | 0.5 | 10 | [17 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Poor | 0.25 | 0 |  |  | Panel Breaker Switching | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | 0 |  | With toilet exhaust | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [7 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
4913 | UN-42 | Band Room | 1st Floor | A | Visual & Performing Arts |  |  | 997 | 9' | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Other (describe) | 10+ |  | 10 | Very Poor | 0.1 | 0 |  | Acoustical panels | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Brick | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Ventilators | 30+ |  | 30 | Good | 0.75 | 0 | [11 empty] | Wet Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | [5 empty] | 0 |  | 5 CPUs | [105 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4914 | UN-43 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 33 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4915 | UN-44 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 74 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4916 | UN-45 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 80 | 8' | Plaster Partitions/on CMU Back-up Wall | 60+ |  | 60 | Poor | 0.25 | 0 |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Other (describe) | 10+ |  | 10 | Poor | 0.25 | 0 |  | Acoustic panels and paint | Suspended Acoustical | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on cmu | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Poor | 0.25 | 0 | [26 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4917 | UN-46 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 34 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4918 | UN-47 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 38 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4919 | UN-48 | Storage | 1st Floor | A | Visual & Performing Arts |  |  | 338 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4920 | UN-49 | Storage | 1st Floor | A | Support |  |  | 272 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4921 | UN-50 | Girls' Water Closet | 1st Floor | A | Support |  |  | 511 | 8' | CMU Back-up Wall | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Ceramic Tile | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 | 0 |  | Two areas of damaged tiles at clean outs | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Tile | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wall-Mounted Lavatories | 22 | 30 | 26 | Good | 0.75 | 6 |  |  | Wall Hung Flush Valve | 22 | 30 | 26 | Good | 0.75 | 12 | [8 empty] | 0 | [17 empty] | 0 |  |  | Solid Surface (Plastic) | 0 | 15 | 7.5 | Good | 0.75 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | 0 |  | Toilet exhaust | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
4922 | UN-51 | Waiting Room | 1st Floor | A | Health Services |  |  | 107 | 9' | [9 empty] | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 | 0 |  | Plaster on cmu | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 | [20 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4923 | UN-52 | Health Office | 1st Floor | A | Health Services |  |  | 321 | 9' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on cmu | Wall-Mounted Lavatories | 41136 |  | 11.5 | Good | 0.75 | 1 |  | Loss faucet | [45 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Window Mounted | 41136 |  | 11.5 | Good | 0.75 | 0 | [17 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 |  | 1 CPU | [105 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4924 | UN-53 | Office | 1st Floor | A | Health Services |  |  | 101 | 9' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4925 | UN-54 | Storage | 1st Floor | A | Health Services |  |  | 24 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4926 | UN-55 | Storage | 1st Floor | A | Health Services |  |  | 27 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4927 | UN-56 | Water Closet | 1st Floor | A | Health Services |  |  | 30 | 10' | [9 empty] | Ceramic Tile | 20+ |  | 20 | Good | 0.75 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Plaster on cmu | Wall-Mounted Lavatories | 16 | 21 | 18.5 | Good | 0.75 | 1 |  |  | Floor Mounted Flush Valve | 16 | 21 | 18.5 | Good | 0.75 | 1 | [8 empty] | 0 | [29 empty] | Fluorescent Linear Surface Mount Fixture | 16 | 21 | 18.5 | Fair | 0.5 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Poor | 0.25 |  |  | Toilet exhaust | [25 empty] | Present - Present - Present - Present - Present - Present - Present
4928 | UN-57 | Newark Evening High School Office | 1st Floor | A | Administration |  |  | 231 | 8' | Plaster on Metal Lath | 60+ |  | 60 | Good | 0.75 | 0 |  |  | Vinyl Composition Tile (VCT) | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 16 | 21 | 18.5 | Good | 0.75 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 | 0 |  | Plaster on cmu | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Unit Ventilators | 30+ |  | 30 | Good | 0.75 | 0 | [11 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 | [8 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 |  |  | 0 |  | 2 CPUs
4929 | UN-58 | Office | 1st Floor | A | Administration |  |  | 85 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4930 | UN-59 | Office | 1st Floor | A | Administration |  |  | 70 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4931 | UN-60 | Storage | 1st Floor | A | Administration |  |  | 117 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4932 | UN-61 | Storage | 1st Floor | A | Support |  |  | 126 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4933 | UN-62 | Storage | 1st Floor | A | Support |  |  | 180 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4934 | UN-110 | Water Closet | 1st Floor | B | Administration |  |  | 40 | 10' | CMU Back-up Wall | 16 | 30 | 23 | Good | 0.75 |  |  |  | Epoxy | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Suspended Acoustical | 22 | 30 | 26 | Poor | 0.25 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 16 | 30 | 23 | Good | 0.75 |  |  |  | Wall-Mounted Lavatories | 22 | 30 | 26 | Good | 0.75 | 1 | [6 empty] | Good | 0.75 | 2 | [6 empty] | Good | 0.75 | 4 | [20 empty] | Solid Surface (Plastic) | 16 | 30 | 23 | Good | 0.75 |  |  |  | Fluorescent Lay-In Fixture (Troffer) | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Panel Breaker Switching | 22 | 30 | 26 | Fair | 0.5 |  |  |  | Other (describe) | 22 | 30 | 26 | Poor | 0.25 |  |  | Supply | [25 empty] | Present
4935 | UN-110 | Boys' Water Closest | 1st Floor | A | Support |  |  | 223 | 9'
4936 | UN-111 | Storage | 1st Floor | B | Support |  |  | 24 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4937 | UN-112 | Womens' Water Closet | 1st Floor | B | Support |  |  | 254 | 9' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
4938 | UN-113 | Athletics Office | 1st Floor | B | Administration |  |  | 279 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4939 | UN-114 | Auxillary Gym | 1st Floor | B | Phys. Ed. (Gym + Storage) |  |  | 1941 | 13' 8" | CMU Back-up Wall | 60+ |  | 60 | Good | 0.75 |  |  |  | Other (describe) | 20+ |  | 20 | Fair | 0.5 |  |  | Rubber | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Other (describe) | 30+ |  | 30 | Good | 0.75 |  |  | Exposed roof deck | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Concrete Block | 60+ |  | 60 | Good | 0.75 |  |  | Brick | [54 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Poor | 0.25 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Vent. AND Radiators | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [10 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 1 |  | Desktops | [70 empty] | Present - Present - Present
4940 | UN-115 | Concession Stand | 1st Floor | B | Phys. Ed. (Gym + Storage) |  |  | 336 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4941 | UN-116 | Boiler Room | 1st Floor | B | Support |  |  | 772 | 10' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4942 | UN-117 | Gymnasium | 1st Floor | B | Phys. Ed. (Gym + Storage) |  |  | 10312 | 28' | CMU Back-up Wall | 16 | 30 | 23 | Good | 0.75 | 0 |  |  | Other (describe) | 16 | 20 | 18 | Fair | 0.5 | 0 |  | Rubber | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Other (describe) | 22 | 30 | 26 | Good | 0.75 | 0 |  | Exposed roof deck | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Concrete Block | 16 | 30 | 23 | Good | 0.75 | 0 | [35 empty] | 0 |  |  | Wall Mounted Electric Water Coolers |  |  |  | Good | 0.75 | 0 | [8 empty] | 0 |  |  | HID Vapor Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Keyed Wall Switches | 22 | 30 | 26 | Fair | 0.5 | 0 |  |  | Other (describe) | 22 | 30 | 26 | Fair | 0.5 | 0 |  | Duct mounted diffusers | [6 empty] | 0 |  |  | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | 0 |  | Missing one | [6 empty] | 0 | Present - Present - Present | [7 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0 | Present - Present - Present - Present
4943 | UN-118 | Custodial Closet | 1st Floor | B | Support |  |  | 23 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4944 | UN-119 | Team Room | 1st Floor | B | Phys. Ed. (Gym + Storage) |  |  | 988 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4945 | UN-120 | Girls\' Locker Room | 1st Floor | B | Phys. Ed. (Gym + Storage) |  |  | 1418 | 12' | CMU Back-up Wall | 16 | 30 | 23 | Good | 0.75 | 0 |  |  | Epoxy | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Other (describe) | 22 | 30 | 26 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Concrete Block | 16 | 30 | 23 | Good | 0.75 | 0 |  |  | Wall-Mounted Lavatories | 22 | 30 | 26 | Good | 0.75 | 1 |  |  | Floor Mounted Flush Valve | 22 | 30 | 26 | Good | 0.75 | 2 |  |  | Wall Hung | 22 | 30 | 26 | Good | 0.75 | 4 |  |  | Other (describe) | 22 | 30 | 26 | Fair | 0.5 | 0 |  | Gang | [9 empty] | Solid Surface (Plastic) | 16 | 30 | 23 | Fair | 0.5 | 0 |  |  | Fluorescent Linear Surface Mount Fixture | 22 | 30 | 26 | Poor | 0.25 | 0 | [11 empty] | Unit Vent. AND Fin Tube | 22 | 30 | 26 | Poor | 0.25 | 0 | [26 empty] | 0 | Present - Present - Present - Present | [133 empty] | 0 | Present - Present - Present - Present - Present
4946 | UN-121 | Boys\' Locker Room | 1st Floor | B | Phys. Ed. (Gym + Storage) |  |  | 1421 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4947 | 201 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 897 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4948 | 202 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 517 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4949 | 203 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 569 | 12' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [11 empty] | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [10 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 3 |  | Desktops | [70 empty] | Present
4950 | 204 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 759 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Acoustical Panel
4951 | 206 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 576 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 |  | Desktops | [70 empty] | Present - Present
4952 | 207 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 700 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | Wall-Mounted Lavatories | 41136 |  | 11.5 | Fair | 0.5 | [48 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [11 empty] | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [9 empty] | 0 | Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 |  | Desktops | [69 empty] | 0 | Present - Present - Present
4953 | 208 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 436 | 11' | [9 empty] | Wood | [17 empty] | Plaster
4954 | 209 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 703 | 11' | [9 empty] | Wood | [17 empty] | Plaster
4955 | 210 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 538 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4956 | 211 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 567 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4957 | 212 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 684 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4958 | 214 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 761 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4959 | 215 | Computer Room | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 836 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | [18 empty] | 0 | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 28 |  | Desktops | [69 empty] | 0 | Present - Present - Present - Present
4960 | 217 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 676 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4961 | 218 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 651 | 12' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present
4962 | 219 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 679 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4963 | 220 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 617 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4964 | 222 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 708 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4965 | 223 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 661 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4966 | 224 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 647 | 12' | [15 empty] | 0 | [17 empty] | 0
4967 | 225 | Classroom | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 882 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Plaster | 0 | 7 | 3.5 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 30+ |  | 30 | Very Poor | 0.1 | [19 empty] | Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 |  | Wall mount | [15 empty] | 7 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present - Present
4968 | UN-63 | Vice Principal\'s Office | 2nd Floor | A | Administration |  |  | 189 | 12' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Asbestos Tile (VAT) | 20+ |  | 20 | Very Poor | 0.1 | 0 |  |  | Other (describe) | 41004 |  | 4.5 | Fair | 0.5 | 0 |  | Stucco wall | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Poor | 0.25 | 0 | [11 empty] | Fin Tube Radiation | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | 0 | [17 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [107 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4969 | UN-64 | Office | 2nd Floor | A | Administration |  |  | 114 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4970 | UN-65 | Storage | 2nd Floor | A | Support |  |  | 29 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4971 | UN-66 | Custodial Closet | 2nd Floor | A | Support |  |  | 28 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4972 | UN-67 | Storage | 2nd Floor | A | Support |  |  | 34 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4973 | UN-68 | Youth Employment Office | 2nd Floor | A | Administration |  |  | 166 | 12' | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Wood | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Good | 0.75 |  |  |  | Plaster/Metal Stud Framing | 60+ |  | 60 | Fair | 0.5 | [57 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  | 2x4 | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 |  |  | 1 desktop | [106 empty] | Present - Present - Present - Present - Present - Present - Present
4974 | UN-69 | Guidance | 2nd Floor | A | Administration |  |  | 846 | 11' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 | [27 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [107 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
4975 | UN-70 | Guidance | 2nd Floor | A | Administration |  |  | 359 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4976 | UN-71 | Storage | 2nd Floor | A | Administration |  |  | 143 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4977 | UN-72 | Storage | 2nd Floor | A | General Classroom (Grades 9-12) |  |  | 82 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4978 | UN-73 | Faculty Water Closet | 2nd Floor | A | Faculty Support |  |  | 25 | 12' | [9 empty] | Ceramic Tile | 20+ |  | 20 | Fair | 0.5 |  |  |  | Ceramic Tile Walls | 10+ |  | 10 | Fair | 0.5 |  |  | Wainscot | Plaster | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Painted brick | Wall-Mounted Lavatories | 30+ |  | 30 | Fair | 0.5 | 1 |  |  | Floor Mounted Flush Valve | 30+ |  | 30 | Fair | 0.5 | 1 | [8 empty] | 0 | [29 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Exhaust grill | [25 empty] | Present - Present - Present - Present - Present - Present - Present
4979 | UN-74 | Room | 2nd Floor | A | Support |  |  | 25 | 8' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4980 | UN-75 | Girls' Water Closet | 2nd Floor | A | Support |  |  | 450 | 11' | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 6 | [8 empty] | 6 | [8 empty] | 0
4981 | UN-76 | Balcony | 2nd Floor | A | Assembly/Large Group (9-12) |  |  | 1372 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4982 | UN-77 | Projector Room | 2nd Floor | A | Assembly/Large Group (9-12) |  |  | 99 | 9' | [9 empty] | Wood | [17 empty] | Plaster
4983 | UN-78 | Boys' Water Closet | 2nd Floor | A | Support |  |  | 235 | 11' | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 4 | [8 empty] | 6 | [8 empty] | 6
4984 | UN-79 | Storage | 2nd Floor | A | Support |  |  | 357 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4985 | UN-80 | Storage | 2nd Floor | A | Support |  |  | 1230 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4986 | UN-81 | Storage | 2nd Floor | A | Support |  |  | 425 | 11' | [15 empty] | 0 | [17 empty] | 0
4987 | 300 | Classroom (English) | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 560 | 12' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [17 empty] | 1 |  | Wall mount | [15 empty] | 3 |  | Desktop | [70 empty] | Present
4988 | 301 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 549 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4989 | 302 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 902 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4990 | 303 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 751 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4991 | 305 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 589 | 12' | [9 empty] | Wood | [17 empty] | Plaster
4992 | 306 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 709 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4993 | 307 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 1000 | 11' | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 |  |  | 2x2 tile | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Plaster | 30+ |  | 30 | Poor | 0.25 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Good | 0.75 |  |  |  | Other (describe) | 60+ |  | 60 | Good | 0.75 |  |  | Brick | In-Counter Lavatories | 30+ |  | 30 | Fair | 0.5 | [48 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Ceiling fan coil | [9 empty] | Other (describe) | 0 | 7 | 3.5 | Fair | 0.5 |  |  | Carbon dioxide | [7 empty] | Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 2 |  | Desktops | [70 empty] | Present - Present
4994 | 308 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 1086 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4995 | 309 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 702 | 12' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Wood | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 |  |  | Dry Chemical | 41136 |  | 11.5 | Fair | 0.5 | 0 | [8 empty] | 0 | Present - Present - Present | [7 empty] | 0 | [8 empty] | 0 |  |  | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [8 empty] | 0 | [26 empty] | 3 |  | Desktops | [69 empty] | 0 | Present - Present - Present
4996 | 311 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 725 | 11' | [9 empty] | Wood | [17 empty] | Plaster
4997 | 312 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 859 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4998 | 313 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 854 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
4999 | 313A | Prep Room | 3rd Floor | A | Administration |  |  | 489 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5000 | 314 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 697 | 12' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Painted Walls | 10+ |  | 10 | Fair | 0.5 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [11 empty] | Dry Chemical | 0 | 7 | 3.5 | Good | 0.75 | [9 empty] | 0 | Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 4 |  | Desktops | [69 empty] | 0 | Present - Present - Present - Present
5001 | 315 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 651 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5002 | 316 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 679 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5003 | 319 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 708 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5004 | 320 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 661 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5005 | 321 | Classroom | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 647 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5006 | UN-82 | N/A | 3rd Floor | A | N/A |  |  | 184 | N/A
5007 | UN-83 | Office | 3rd Floor | A | Administration |  |  | 117 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5008 | UN-84 | Storage | 3rd Floor | A | General Classroom (Grades 9-12) |  |  | 225 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5009 | UN-85 | Custodial Closet | 3rd Floor | A | Support |  |  | 26 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5010 | UN-86 | Office | 3rd Floor | A | Administration |  |  | 168 | 11' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5011 | UN-87 | Computer Room | 3rd Floor | A | Technological Literacy |  |  | 958 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5012 | UN-88 | Library | 3rd Floor | A | Media Center |  |  | 3486 | 11' 6" | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Carpet | 41228 |  | 13 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Ceiling diffusers | [24 empty] | 0 | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 9 |  | Desktops | [69 empty] | 0 | Present - Present - Present - Present - Present - Present - Present
5013 | UN-89 | Med Ctr Office | 3rd Floor | A | Media Center |  |  | 195 | 11' 10" | [6 empty] | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Plaster | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Metal Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [56 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 | 0 |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 | 0 |  | Ceiling diffusers | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [26 empty] | 1 | [71 empty] | 0
5014 | UN-90 | Med Ctr Office | 3rd Floor | A | Media Center |  |  | 219 | 11' 10" | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [62 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 | [98 empty] | 0
5015 | UN-91 | Conference Room | 3rd Floor | A | Media Center |  |  | 207 | 11' 10" | [9 empty] | Carpet | 41228 |  | 13 | Good | 0.75 |  |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 |  |  |  | Suspended Acoustical | 30+ |  | 30 | Good | 0.75 |  |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | [66 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Good | 0.75 |  |  | P | Other (describe) | 30+ |  | 30 | Good | 0.75 |  |  | Ceiling diffusers | [25 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | [36 empty] | 2 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present - Present - Present
5016 | UN-92 | Office | 3rd Floor | A | Media Center |  |  | 199 | 11' 10" | [9 empty] | Carpet | [17 empty] | Acoustical Panel
5017 | UN-93 | Storage | 3rd Floor | A | Media Center |  |  | 262 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5018 | UN-94 | Mens' Water Closet | 3rd Floor | A | Media Center |  |  | 65 | 9' | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 1
5019 | UN-95 | Womens' Water Closet | 3rd Floor | A | Media Center |  |  | 65 | 9' | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 1 | [8 empty] | 1 | [8 empty] | 0
5020 | UN-96 | Storage | 3rd Floor | A | Media Center |  |  | 51 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5021 | UN-97 | Storage | 3rd Floor | A | Media Center |  |  | 34 | 11' 10" | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5022 | UN-98 | Computer Room | 3rd Floor | A | Technological Literacy |  |  | 983 | 10' | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Good | 0.75 | 0 |  |  | Acoustical Panel | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Wood Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 | 0 |  | Plaster on masonry | [54 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Unit Vent. AND Fin Tube | 30+ |  | 30 | Fair | 0.5 | 0 | [27 empty] | Present - Present - Present - Present - Present - Present - Present | [19 empty] | Hardwired CAT 5/6 | 10+ |  | 10 | Fair | 0.5 | 0 | [35 empty] | 24 |  | Desktops | [70 empty] | Present - Present - Present - Present - Present - Present - Present
5023 | UN-99 | Boys' Water Closet | 3rd Floor | A | Support |  |  | 281 | 9' | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 4 | [8 empty] | 6 | [8 empty] | 6
5024 | UN-100 | Faculty Room | 3rd Floor | A | Faculty Support |  |  | 281 | 12' | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 |  |  |  | Vinyl Composition Tile (VCT) | 20+ |  | 20 | Good | 0.75 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  |  | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on masonry | [54 empty] | Fluorescent Linear Pendant Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Unit Ventilators | 30+ |  | 30 | Poor | 0.25 |  |  |  | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | 0 | [17 empty] | 0 | Present - Present - Present - Present - Present | [133 empty] | 0 | Present - Present - Present - Present - Present
5025 | UN-101 | Cafeteria | 3rd Floor | A | Food Services (9-12) |  |  | 4879 | 15' 5" | Brick, Exposed/Unfinished | 60+ |  | 60 | Fair | 0.5 | 0 |  |  | Unfinished | 20+ |  | 20 | Poor | 0.25 | 0 |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 | 0 |  |  | Suspended Acoustical | 30+ |  | 30 | Fair | 0.5 | 0 |  | Concealed spline | Wood/Metal Frame | 20+ |  | 20 | Fair | 0.5 | 0 |  |  | Plaster/Metal Stud Framing | 60+ |  | 60 | Fair | 0.5 | 0 | [38 empty] | Other (describe) | 16 | 21 | 18.5 | Fair | 0.5 | 0 |  | Floor mount stainless steel | [9 empty] | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Good | 0.75 | 0 |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 | [11 empty] | Window Mounted | 0 | 7 | 3.5 | Good | 0.75 | 0 | [17 empty] | 0 | Present - Present - Present - Present - Present - Present | [34 empty] | 0 | Present | [97 empty] | 0 | Present - Present - Present - Present - Present - Present | [25 empty] | 0 | Present | [7 empty] | 0 | Present
5026 | UN-102 | Kitchen | 3rd Floor | A | Food Services (9-12) |  |  | 703 | 12' | [9 empty] | Unfinished | 20+ |  | 20 | Poor | 0.25 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Wood/Wood Frame | 20+ |  | 20 | Poor | 0.25 |  |  |  | Plaster/Metal Stud Framing | 60+ |  | 60 | Poor | 0.25 |  |  |  | Stainless Steel Sinks | 41136 |  | 11.5 | Good | 0.75 | [48 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Good | 0.75 |  |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Ceiling diffusers | [25 empty] | Present - Present - Present - Present - Present - Present - Present | [161 empty] | Present - Present | [8 empty] | Present
5027 | UN-103 | Storage | 3rd Floor | A | Food Services (9-12) |  |  | 12 | 12' | [9 empty] | Unfinished | [17 empty] | Plaster
5028 | UN-104 | Storage | 3rd Floor | A | Food Services (9-12) |  |  | 74 | 12' | [9 empty] | Unfinished | [17 empty] | Plaster
5029 | UN-105 | N/A | 3rd Floor | A | N/A |  |  | 359 | N/A
5030 | UN-106 | N/A | 3rd Floor | A | N/A |  |  | 356 | N/A
5031 | UN-107 | Girls' Water Closet | 3rd Floor | A | Support |  |  | 242 | 9' | [9 empty] | Ceramic Tile | [17 empty] | Plaster | [32 empty] | 6 | [8 empty] | 6 | [8 empty] | 0
5032 | UN-108 | Office | 3rd Floor | A | Administration |  |  | 220 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
5033 | UN-109 | Custodial Closet | 3rd Floor | A | Support |  |  | 25 | 12' | [9 empty] | Vinyl Composition Tile (VCT) | [17 empty] | Plaster
12616 | UN-122 | Team Room | 1st Floor | A | Phys. Ed. (Gym + Storage) |  |  | 943 | 12'
INTERIORs INFORMATION
Lobbys | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
34 | A | @ UN-40 (Auditorium) | 1st | [14 empty] | None | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  | Terrazzo tiles, cracks in some places | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Marble wainscot | Plaster | 30+ |  | 30 | Fair | 0.5 | [12 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on CMU | [9 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | [28 empty] | Present | [17 empty] | Present | Camera | [7 empty] | Present
35 | B | @ UN-117 (Gymnasium) | 1st | [6 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Storefront window type | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  |  | Other (describe) | 0 | 7 | 3.5 | Good | 0.75 |  |  | Metal strips panel | [9 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Brick veneer | [9 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 22 | 30 | 26 | Fair | 0.5 |  |  | Ceiling mounted diffusers | [16 empty] | Present | [26 empty] | Present
Corridors | [9 empty] | Floor Finish | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Standpipes | [8 empty] | Partitions | [8 empty] | Plumbing Fixtures - Drinking Fountains | [8 empty] | Lockers | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
112 | A | @ UN-7 (Conference Room) | 1st | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Brick wainscot | Suspended Acoustical | 0 | 7 | 3.5 | Good | 0.75 |  |  | Few tiles need replacement | [9 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on CMU | [9 empty] | Other (describe) | 16 | 30 | 23 | Fair | 0.5 |  |  | Triple tier lockers | Fluorescent Lay-In Fixture (Troffer) | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 | [11 empty] | N/A | [16 empty] | Present | [17 empty] | Present | Camera | [7 empty] | Present
113 | B | @ UN-80 (Storage) | 2nd | [6 empty] | Solid Terrazzo | 20+ |  | 20 | Fair | 0.5 |  |  | Cracks in some areas | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Brick wainscot | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  | Decorative metal ceiling, | [9 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | Plaster on CMU | Wall Mounted Stainless Steel Drinking Fountains | 41136 |  | 11.5 | Fair | 0.5 |  |  |  | Other (describe) | 16 | 30 | 23 | Fair | 0.5 |  |  | Triple tier lockers | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  | 2x4, 2 needs replacment | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 |  |  |  | Dry Chemical | 41136 |  | 11.5 | Good | 0.75 | [10 empty] | Present | [17 empty] | Present | [8 empty] | Present
167
Stairs | [9 empty] | Exterior Walls - Interior Assembly | [8 empty] | Stair Construction | [8 empty] | Wall Finish | [8 empty] | Ceiling Finish | [8 empty] | Tread Finish | [8 empty] | Landing Finish | [8 empty] | Interior Door | [8 empty] | Standpipes | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | HVAC Terminal Units | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | Fire-Suppression (Sprinklers), Water-Based | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
108 | A | @ 114 (Classroom) | 1st-3rd | [6 empty] | Plaster on Metal Lath | 60+ |  | 60 | Fair | 0.5 |  |  | Brick veneer with cmu backup | Steel Pan | 30+ |  | 30 | Fair | 0.5 |  |  |  | Painted Walls with Wainscot | 10+ |  | 10 | Fair | 0.5 |  |  | Brick wainscot | Plaster | 30+ |  | 30 | Fair | 0.5 |  |  |  | Exposed Concrete | 30+ |  | 30 | Fair | 0.5 |  |  | Painted | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  | Epoxy | Labeled Metal/Metal Frames | 41070 |  | 8 | Good | 0.75 | [12 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  | Cover missing | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Fan coil unit | [16 empty] | Present
109 | B | @ UN-32 (Weight Room) | 1st-3rd | [6 empty] | Other (describe) | 60+ |  | 60 | Fair | 0.5 |  |  | None | Steel Pan | 30+ |  | 30 | Fair | 0.5 |  |  |  | Painted Walls | 10+ |  | 10 | Poor | 0.25 |  |  |  | Other (describe) | 30+ |  | 30 | Fair | 0.5 |  |  | Cast in place concrete | Exposed Concrete | 30+ |  | 30 | Fair | 0.5 |  |  | Epoxy | Terrazzo | 30+ |  | 30 | Fair | 0.5 |  |  | Epoxy | Metal/Metal Frame | 20+ |  | 20 | Fair | 0.5 |  |  | 1 1/2 rated | [9 empty] | Fluorescent Linear Surface Mount Fixture | 41136 |  | 11.5 | Fair | 0.5 |  |  | Lens missing | Keyed Wall Switches | 30+ |  | 30 | Fair | 0.5 |  |  |  | Cast Iron Radiators | 30+ |  | 30 | Fair | 0.5 | [19 empty] | Present
162
163
Elevators | [9 empty] | Elevator | [8 empty] | Lighting Fixtures | [8 empty] | Lighting Controls | [8 empty] | Fire Extinguishing Systems | [8 empty] | Fire Detection and Alarm Systems | [8 empty] | CCTV | [8 empty] | Voice Communication Terminal Equipment | [8 empty] | Car Load Capacity | [8 empty] | Elevator Equipment and Controls
Int ID | Index | Location | Level | Notes | [5 empty] | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes | Description | Age |  | #VALUE! | Condition | FALSE | Quantity | Checkbox | Notes
12 | A | @ UN-50 (Girls' Water Closet) | 1st-3rd | [6 empty] | Hydraulic | 30+ |  | 30 | Fair | 0.5 | 0 |  |  | Incandescent Surface Mount Fixture | 30+ |  | 30 | Poor | 0.25 | 0 |  |  | Toggle Wall Switches | 30+ |  | 30 | Fair | 0.5 | 0 | [8 empty] | 0 | [8 empty] | 0 | Present | Poor condition | [6 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  | 2500lbs | [6 empty] | 0

## Master File (Systems)
Systems | Question | Value1 |  | Average1 | Systems | Question | Value1 |  | Average1
Systems | Seg ID | 849 |  |  | InfoTech | Seg ID | 339
| Bldg.Phase | A |  |  |  | Bldg.Phase | A
| Original | 1 |  |  |  | Original | 1
| Addition | 1 |  |  |  | Addition | 1
| Year Built | 1926, 1929 |  |  |  | Year Built | 1926, 1929
Domestic Water Heaters | Location | Un27 |  |  | Entrance Facilities (Demarc or Cable Vault) | Location
| Description | Fuel/Fired Water Heater |  |  |  | Description
| Age | 0 | 7 | 3.5 |  | Age
| Condition | Good |  | 0.75 |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Gas, 6 hot water storage tanks, copper piping |  |  |  | Notes
Sanitary Drainage | Location | Roof |  |  | Main Dist. Facility (MDF) | Location | Above Ground Level Floor
| Description | Sanitary Sewers |  |  |  | Description | Floor mount rack
| Age | 60+ |  | 60 |  | Age | 41067 |  | 6.5
| Condition | Fair |  | 0.5 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Bathroom vents iping |  |  |  | Notes | Un88
Building Support (other) Plumbing Systems | Location | Roof |  |  | MDF, HVAC Terminal Units | Location
| Description | Stormwater Area Drains |  |  |  | Description | Other (describe)
| Age | 60+ |  | 60 |  | Age | 22 | 30 | 26
| Condition | Poor |  | 0.25 |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | Ceiling difusers
Fuel Piping | Location | Un27 |  |  | MDF, Packaged Terminal Air Conditioner | Location
| Description | Gas Piping |  |  |  | Description | Other (describe)
| Age | 0 | 15 | 7.5 |  | Age | 41136 |  | 11.5
| Condition | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | Wall mount
Fuel Pumps | Location |  |  |  | Inter. Data Facility (IDF #1) | Location | 326
| Description |  |  |  |  | Description | Floor mount closet
| Age |  |  |  |  | Age | 41067 |  | 6.5
| Condition |  |  |  |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | Mdf2
Fuel Storage Tanks | Location |  |  |  | IDF #1, HVAC Terminal Units | Location
| Description |  |  |  |  | Description | Other (describe)
| Age |  |  |  |  | Age | 22 | 30 | 26
| Condition |  |  |  |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | Ceiling diffusers
Fuel Fired Boilers | Location | UN/27 |  |  | IDF #1, Packaged Terminal Air Conditioner | Location
| Description | Gas/Fired Boilers |  |  |  | Description | Window Mounted
| Age | 0 | 15 | 7.5 |  | Age | 41136 |  | 11.5
| Condition | Good |  | 0.75 |  | Condition | Poor |  | 0.25
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Furnaces | Location |  |  |  | Inter. Data Facility (IDF #2) | Location | Un81
| Description |  |  |  |  | Description | Floor mount rack
| Age |  |  |  |  | Age | 41067 |  | 6.5
| Condition |  |  |  |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Unit Ventilators | Location |  |  |  | IDF #2, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | N/a
Fan Coil Units | Location |  |  |  | IDF #2, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | N/a
Water Chillers | Location |  |  |  | Inter. Data Facility (IDF #3) | Location | Un29
| Description |  |  |  |  | Description | Wall mount
| Age |  |  |  |  | Age | 41067 |  | 6.5
| Condition |  |  |  |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Cooling Towers | Location |  |  |  | IDF #3, HVAC Terminal Units | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | N/a
Packaged Terminal Air Conditioner | Location |  |  |  | IDF #3, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | N/a
Hydronic Piping System | Location | UN/27 |  |  | Inter. Data Facility (IDF #4) | Location | Un62
| Description | Zoned Hot Water System |  |  |  | Description | Wall mount
| Age | 0 | 15 | 7.5 |  | Age | 41067 |  | 6.5
| Condition | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | Idf1
Pumps | Location | Un27 |  |  | IDF #4, HVAC Terminal Units | Location
| Description | Hydronic Pumps |  |  |  | Description | Other (describe)
| Age | 0 | 15 | 7.5 |  | Age | 22 | 30 | 26
| Condition | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | Ceiling diffusers
Steam Piping System | Location |  |  |  | IDF #4, Packaged Terminal Air Conditioner | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes | N/a
HVAC Air Distribution | Location |  |  |  | Inter. Data Facility (IDF #5) | Location | 215
| Description |  |  |  |  | Description | Wall mount
| Age |  |  |  |  | Age | 41067 |  | 6.5
| Condition |  |  |  |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox | Secure
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Air Handling Units | Location | Roof |  |  | IDF #5, HVAC Terminal Units | Location
| Description | Package Rooftop Units (RTU) |  |  |  | Description | Unit Ventilators
| Age | 21 | 30 | 25.5 |  | Age | 30+ |  | 30
| Condition | Very Poor |  | 0.1 |  | Condition | Fair |  | 0.5
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Split system |  |  |  | Notes
HVAC Fans | Location | Roof |  |  | IDF #5, Packaged Terminal Air Conditioner | Location
| Description | Other (describe) |  |  |  | Description | Window Mounted
| Age | 0 | 10 | 5 |  | Age | 0 | 7 | 3.5
| Condition | Good |  | 0.75 |  | Condition | Good |  | 0.75
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes | Roof exhaust fan |  |  |  | Notes
Fire/Suppression (Sprinklers), Water/Based | Location |  |  |  | Backbone Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Fire/Suppression (Standpipes), Water/Based | Location |  |  |  | Horizontal Cable Dist. | Location
| Description |  |  |  |  | Description
| Age |  |  |  |  | Age
| Condition |  |  |  |  | Condition
| CheckBox |  |  |  |  | CheckBox
| Quantity |  |  |  |  | Quantity
| Voltage |  |  |  |  | Voltage
| Power Output |  |  |  |  | Power Output
| Elec Power |  |  |  |  | Elec Power
| Notes |  |  |  |  | Notes
Facility Power Generation, Packaged Generator Assemblies | Location | Un27
| Description | Gas Engine Generators
| Age | 16 | 30 | 23
| Condition | Poor |  | 0.25
CheckBox
Quantity
| Voltage | 208
| Power Output | 49kva
Elec Power
Notes
Facility Power Generation (Alternative Sources) | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Electrical Service & Distribution | Location | Un27
| Description | D5010 120
| Age | 60+ |  | 60
| Condition | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | 3000 amps
Voice Communication Terminal Equipment | Location | Un14
| Description | PDX/Key Systems
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Distributed AV Communication (Paging) Systems | Location | Un14
| Description | Public Address and Mass Notification Systems
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Video Surveillance Systems | Location | Un28
| Description | Digital Video Recorders
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Fire Detection and Alarm Systems | Location | Un14
| Description | Fire Alarm Annunciation Panels
| Age | 0 | 10 | 5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Integrated Automation (BMS/EMS) Systems | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Other Equipment | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes

## Master File (Exterior)
Systems | Question | Value1 |  | Average1 | Value2 |  | Average2 | Value3 | Average3 | Systems | Question | Value1 |  | Average1
Exterior | Seg ID | 1156 |  |  | 1172 |  |  | 2349 |  | SiteElements | Seg ID | 392
| Bldg.Phase | A |  |  | B |  |  | C |  |  | Bldg.Phase | A
| Original | 1 |  |  | 0 | [5 empty] | Original | 1
| Addition | 1 |  |  | 1 | [5 empty] | Addition | 1
| Year Built | 1926, 1929 |  |  | 1982 | [5 empty] | Year Built | 1926, 1929
(Foundation) Walls for Subgrade Enclosures, Primary | Location | Typical |  |  | Typical |  |  |  |  | Roadways | Location | West
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place | [5 empty] | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 | 16 | 30 | 23 |  |  |  | Age | 22 | 30 | 26
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  |  |  | Condition | Fair |  | 0.5
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes |  |  |  | Partial cast in place foundation | [5 empty] | Notes
(Foundation) Walls for Subgrade Enclosures, Secondary | Location | [8 empty] | Parking Lots | Location | West and North
| Description | [9 empty] | Description | Asphalt (Bituminous)
| Age | [9 empty] | Age | 22 | 30 | 26
| Condition | [9 empty] | Condition | Poor |  | 0.25
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | [9 empty] | Notes
Standard Slabs On Grade, Primary | Location | Typical |  |  | Typical |  |  |  |  | Pedestrian Plazas and Walkways, Primary | Location | South
| Description | Concrete, Cast/In/Place |  |  | Concrete, Cast/In/Place | [5 empty] | Description | Concrete, CIP
| Age | 60+ |  | 60 | 16 | 30 | 23 |  |  |  | Age | 22 | 30 | 26
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  |  |  | Condition | Poor |  | 0.25
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | [9 empty] | Notes
Standard Slabs On Grade, Secondary | Location | [8 empty] | Pedestrian Plazas and Walkways, Secondary | Location | South
| Description | [9 empty] | Description | Concrete, CIP
| Age | [9 empty] | Age | 16 | 21 | 18.5
| Condition | [9 empty] | Condition | Fair |  | 0.5
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | [9 empty] | Notes
Floor Construction, Primary | Location | Typical |  |  | Typical |  |  |  |  | Athletic, Recreational, and Playfield Areas, Primary | Location | Interior garden
| Description | Concrete, CIP Beams and Slab |  |  | Concrete, CIP Beams and Slab | [5 empty] | Description | Other (describe)
| Age | 60+ |  | 60 | 16 | 30 | 23 |  |  |  | Age | 30+ |  | 30
| Condition | Fair |  | 0.5 | Fair |  | 0.5 |  |  |  | Condition | Very Poor |  | 0.1
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | [9 empty] | Notes | Science garden adjacent to atrium unusable , community relations officer suggest if the garden can b
Floor Construction, Secondary | Location | Boiler room | [7 empty] | Athletic, Recreational, and Playfield Areas, Secondary | Location
| Description | Concrete, Waffle Slab | [8 empty] | Description
| Age | 60+ |  | 60 | [6 empty] | Age
| Condition | Fair |  | 0.5 | [6 empty] | Condition
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | [9 empty] | Notes
Roof Construction, Structural Frame, Primary | Location | Typical |  |  | Typical |  |  |  |  | Site Lighting, Primary | Location | Typical
| Description | Concrete, CIP |  |  | Concrete, CIP | [5 empty] | Description | Pole Mounted H.I.D.
| Age | 60+ |  | 60 | 16 | 30 | 23 |  |  |  | Age | 41136 |  | 11.5
| Condition | Good |  | 0.75 | Fair |  | 0.5 |  |  |  | Condition | Good |  | 0.75
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes |  |  |  | Unknown | [5 empty] | Notes
Roof Construction, Structural Frame, Secondary | Location | [8 empty] | Site Lighting, Secondary | Location | Typ
| Description | [9 empty] | Description | Building Mounted H.I.D.
| Age | [9 empty] | Age | 30+ |  | 30
| Condition | [9 empty] | Condition | Fair |  | 0.5
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | [9 empty] | Notes
Exterior Walls / Exterior Assembly, Primary | Location | Typical |  |  | Typical |  |  |  |  | Playground Surface | Location | East
| Description | Brick Veneer w/ Steel Stud |  |  | Brick Veneer w/ Steel Stud | [5 empty] | Description | Asphalt (Bituminous)
| Age | 60+ |  | 60 | 16 | 30 | 23 |  |  |  | Age | 30+ |  | 30
| Condition | Fair |  | 0.5 | Poor |  | 0.25 |  |  |  | Condition | Poor |  | 0.25
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | Brick veneer with cmu backup |  |  | Brick veneer with cmu backup | [5 empty] | Notes
Exterior Walls / Exterior Assembly, Secondary | Location |  |  |  | Gym upper wall |  |  |  |  | Playground Equipment | Location | North
| Description |  |  |  | Other (describe) | [5 empty] | Description | B/Ball Backstops
| Age |  |  |  | 16 | 30 | 23 |  |  |  | Age | 22 | 30 | 26
| Condition |  |  |  | Poor |  | 0.25 |  |  |  | Condition | Very Poor |  | 0.1
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes |  |  |  | Translucent sandwich panels | [5 empty] | Notes
Exterior Windows, Primary | Location | Typical |  |  | Entrance#2 |  |  |  |  | TCUs | Location
| Description | Other (describe) |  |  | Other (describe) | [5 empty] | Description
| Age | 30+ |  | 30 | 22 | 30 | 26 |  |  |  | Age
| Condition | Fair |  | 0.5 | Poor |  | 0.25 |  |  |  | Condition
| CheckBox | [9 empty] | CheckBox
| Quantity | [9 empty] | Quantity
| Voltage | [9 empty] | Voltage
| Power Output | [9 empty] | Power Output
| Elec Power | [9 empty] | Elec Power
| Notes | Aluminum single hung |  |  | Storefront type | [5 empty] | Notes
Exterior Windows, Primary / Glazing | Location
| Description | Glass, Double Pane (Insulated) |  |  | Glass, Double Pane (Insulated)
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | 1 inch
Exterior Windows, Primary / Accessories | Location
Description
Age
Condition
| CheckBox | Security Grilles
Quantity
Voltage
Power Output
Elec Power
| Notes | First floor
Exterior Windows, Secondary | Location | Typ
| Description | Other (describe)
| Age | 30+ |  | 30
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Alum with sliding
Exterior Windows, Secondary / Glazing | Location
| Description | Glass, Single Pane
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Windows, Secondary / Accessories | Location
Description
Age
Condition
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Primary | Location | Typical |  |  | Typical
| Description | Fiber Reinforced Panel (FRP) |  |  | Steel (Hollow) |  |  | Wood
| Age | 0 | 15 | 7.5 | 16 | 30 | 23
| Condition | Good |  | 0.75 | Poor |  | 0.25
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Exterior Doors, Secondary | Location | Emergency exit
| Description | Steel (Hollow)
| Age | 0 | 15 | 7.5
| Condition | Good |  | 0.75
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roofing, Primary | Location | Typical |  |  | Typical
| Description | Polyurethane, Spray Applied |  |  | Polyurethane, Spray Applied
| Age | 41136 |  | 11.5 | 22 | 30 | 26
| Condition | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Multiple areas need repair
Roofing, Secondary | Location
| Description | Asphalt Shingle
| Age | 41136 |  | 11.5
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes
Roof (Accessories) Supplementary Components / Flashing and Trim | Location | Typical |  |  | Typical
| Description | Aluminum |  |  | Aluminum
| Age | 41136 |  | 11.5 | 41136 |  | 11.5
| Condition | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | With old peripheral metal flashing |  |  | Parapet clay tiles
Roof (Accessories) Appurtenances / Rainwater Management (Gutters, Downspouts) | Location | Typical |  |  | Typical
| Description | Other (describe) |  |  | Other (describe)
| Age | 30+ |  | 30 | 22 | 30 | 26
| Condition | Fair |  | 0.5 | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
| Notes | Cast iron |  |  | Cast iron
Lightning Protection | Location | Chimney at North
| Description | Tape, Continuous
| Age | 22 | 30 | 26
| Condition | Fair |  | 0.5
CheckBox
Quantity
Voltage
Power Output
Elec Power
Notes